## Slide 1: Auxiliary Service Chains for YE1.
Existing YE1 chains have an available cross section for services of 3,400cm2 per chain, with an occupancy of more than 85%.
An additional service chain is proposed for YE1 detector services (post LS3), essentially for CO2 cooling. A free cross section of 1000cm2 is retained (4x110mm CO2 vacuum insulated lines, 120cm2 for dry-air pipes plus about 400cm2 for YN detectors).
The chain is located on the near-side of the UXC5 balconies, at level X3, both (-) & (+) ends. It spans over 10m, to let a full opening of the YE1 disk. A second chain on the far side can be installed if necessary (check interference with survey line).
A patch-panel on the detector towers is foreseen, same X3 level. It would reduce the available space in height for the two electronics racks.

## Slide 2
YE1
X3
X2
X4
NEAR SIDE
Space left
for racks
Patch panel
CO2 piping

## Slide 3: Typical medium size cable chain (YE3 type)

## Slide 4
YE+1
YE(-)1
HGC
UL 56
USC
Ex control room
UXC
Transfer lines
USC-UXC
Near side
CO2 pipes-balcony
Cable chains
CO2 pipes-balcony
Cable chains
Far side
Manifold
Manifold
X0 level
HGC Cooling System
concept
OD 250 mm
OD 150 mm
OD 110 mm
OD 65 mm

## Slide 5
UL 56
USC
Ex control room
UXC
Near side
Far side
X0 level
YE+1

## Slide 6
CO2 pipes-balcony
Far side
Manifold
UL 56
YE+1
YE(-)1

## Slide 7
YE+1
HGC
Cable chain
1
2
3
4