|  | EUROPEAN ORGANIZATION FOR NUCLEAR RESEARCH COMPACT MUON SOLENOID EXPERIMENT |  |
| --- | --- | --- |
| Gas leak test report |  |  |

| IDENTIFICATION |  |
| --- | --- |
| Date | 10.03.2005 |
| Barrel / Endcap ID | YE-1 |
| Circuit System | EE manifold and cooling circuits |
| Test preformed by | Soteb |
| CERN representative supervising | Lasse Isaksen |
| Initial test pressure | 14 bar |
| Time test pressure maintained | 23 Hours 32 min |
| Pressure drop during test period | 689 mbar |
| Pressure drop during 1 hour | 29.28 mbar/hour |
| Volume | 230 liter |
| Leak rate with temperature correction | 1.88 mbar*l/sec |

| DECISION |  |  |  |
| --- | --- | --- | --- |
| DECISION |  |  |  |
| Contractors decision |  | Requester’s decision |  |
| Reject Approved |  | Rejected Approved |  |
| Name |  | Name |  |
| Date |  | Date |  |

Summary:

Two flowlimiters on the nose region, had to be refitted before the test.

Figure.1: Capture of computer screen at end of test.

Figure.2: Graph created from test data.

| Leak test EE cooling YE-1 |  |  |
| --- | --- | --- |
| fuite 0.02928 bars par heure |  |  |
| 0.689062 bars en 23 heures 32 min |  |  |
| Key data in stabil time zone |  |  |
| Max temp Haute |  |  |
| Min temp Haute |  |  |
| Delta T |  |  |
| Max temp Bas |  | 26.614786 |
| Min temp Bas |  | 26.438545 |
| Delta T |  | 0.176241 |
| Max press bar |  | 13.984 |
| Min press bar |  | 13.7625 |
| Delta bar |  | 0.22125 |
| Delta mbar |  | 221.25 |
| Volume liter |  | 230 |
| Time in stabile Zone h |  | 6 |
| Total time test h |  | 23.32 |
| Leak rate stable time zone mbar*l/sec |  | 2.356 |
| Leak rate total test time mbar*l/sec |  | 1.888 |
| Max press bar total test time |  | 14.4515625 |
| Min press bar total test time |  | 13.76250 |
| Delta P bar total test time |  | 0.6891 |
| Delta P mbar total test time |  | 689.0625 |
| T1, Start temp in stable zone |  | 299.614786 |
| T2, End temp in stable zone |  | 299.438545 |
| Temp correction factor T2/T1 |  | 0.999411775 |
| Leak rate with temp corr |  | 1.886687041 |

Table.1: Data used for calulation.