I just discovered a document was missing from the document set I posted earlier. This document is titled "coolingYE3_26apr12.pdf" and is now posted with the other files at ftp://ftp.psl.wisc.edu/cms/ye3upgrade/RE4cooling/pdfs_powerpoint/. Page 9 has a useful schematic of the new manifold circuit.

I also added four drawings of the YE3 manifold. The new manifolds will connect to the YE3 manifold where the tower racks are currently connected. These drawings show the rack port locations in the YE3 manifold and will be useful when looking for the main supply and return ports for the new manifold. The new manifold will supply the RPC and the racks in the tower. These YE3 manifold drawings are numbers 5599807e.pdf, 808e.pdf, 813e.pdf, and 814e.pdf.

As Wojciech looked at Dan's drawings he saw that for sure frontal access is
needed for fixing the mini-manifolds to the green structure (on the
non-IP side).
He was not sure what about the installation of the flexible pipes (from the
mini-manifolds to the big manifold). He suggested Dan could answer this better.

Dan answered Wojciech was correct. “Mounting the manifolds requires "frontal access to 
the non-IP side of the YE3 disks". After the manifolds are mounted, the 
hoses that are currently routed to the racks need to be rerouted to the 
mini-manifolds. Then new hoses need to be run from the mini-manifold 
to the racks. I believe it is possible to do this without frontal 
access, but it would be more convenient to do this with frontal access.”

We just finished the meeting with Austin, Gerd, Patrice and Martin about the ZEC manpower in April.
We agreed that 2 additional ZEC technicians will come for the first 2 weeks of April travelling to CERN on 03.04 and going back to Poland on 19.04. Therefore we will have them for 11 working days between 04.04 and 18.04.

Additionally, according to the latest CMS Master plan we will have frontal access to YE+3 non-IP side for 5 working days after Easter - from 04.04 till 10.04.2013 included. On 11.04. we will lose the access but they will have almost a week to work with lateral access from the periphery and staircase. Gerd also suggested that if they finish earlier with the positive Endcap they can do whatever can be done in close configuration on the negative Endcap.