## 38"flow tests (2.8 lpm)
total | restrictor R1/T1 | cooling tubes | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | total R2/T2 | restrictor R2/T2 | G.P.M. R2/T2 | total R2/T3 | restrictor R2/T3 | G.P.M. R2/T3 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10% | total R1/T1 | restrictor R1/T1 | cooling tubes R1/T1 | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | total R2/T2 | restrictor R2/T2 | G.P.M. R2/T2 | total R2/T3 | restrictor R2/T3 | G.P.M. R2/T3 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10% | total R1/T1 | restrictor R1/T1 | cooling tubes R1/T1 | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | total R2/T2 | restrictor R2/T2 | G.P.M. R2/T2 | total R2/T3 | restrictor R2/T3 | G.P.M. R2/T3 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10%
0.6895 | 0.34475 | 0.34475 | 1.9684 | 0.6895 | 0.34475 | 2.0441 | 0.6895 | 0.48265 | 2.1576 | 0.6895 | 0.4137 | 2.1576 | 0.6895 | 0.4137 | 2.1198 | 0.75706 | 1.379 | 0.75706 | 4.137 | 2.5551 | 0.6895 | 3.1229 | 0.6895 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 10 | 5 | 5 | 0.52 | 10 | 5 | 0.54 | 10 | 7 | 0.57 | 10 | 6 | 0.57 | 10 | 6 | 0.56 | 0.2 | 20 | 0.2 | 60 | 0.675 | 10 | 0.825 | 10
1.0342 | 0.5516 | 0.48265 | 2.3469 | 1.0342 | 0.5516 | 2.4604 | 1.0342 | 0.6895 | 2.3847 | 1.0342 | 0.6895 | 2.4604 | 1.0342 | 0.6895 | 2.4226 | 0.94632 | 1.379 | 0.94632 | 4.137 | 2.5551 | 1.379 | 3.1229 | 1.379 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 15 | 8 | 7 | 0.62 | 15 | 8 | 0.65 | 15 | 10 | 0.63 | 15 | 10 | 0.65 | 15 | 10 | 0.64 | 0.25 | 20 | 0.25 | 60 | 0.675 | 20 | 0.825 | 20
1.379 | 0.5516 | 0.8274 | 2.574 | 1.379 | 0.8274 | 2.6497 | 1.379 | 0.9653 | 2.574 | 1.379 | 0.9653 | 2.574 | 1.379 | 0.9653 | 2.574 | 1.1356 | 1.379 | 1.1356 | 4.137 | 2.5551 | 2.0685 | 3.1229 | 2.0685 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 20 | 8 | 12 | 0.68 | 20 | 12 | 0.7 | 20 | 14 | 0.68 | 20 | 14 | 0.68 | 20 | 14 | 0.68 | 0.3 | 20 | 0.3 | 60 | 0.675 | 30 | 0.825 | 30
1.7237 | 1.1032 | 0.62055 | 2.6876 | 1.7237 | 1.1032 | 2.7633 | 1.7237 | 1.31 | 2.6497 | 1.7237 | 1.2411 | 2.7254 | 1.7237 | 1.2411 | 2.6876 | 1.3249 | 1.379 | 1.3249 | 4.137 | 2.5551 | 2.758 | 3.1229 | 2.758 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 25 | 16 | 9 | 0.71 | 25 | 16 | 0.73 | 25 | 19 | 0.7 | 25 | 18 | 0.72 | 25 | 18 | 0.71 | 0.35 | 20 | 0.35 | 60 | 0.675 | 40 | 0.825 | 40
2.0685 | 1.5169 | 0.5516 | 2.7254 | 2.0685 | 1.448 | 2.7633 | 2.0685 | 1.6548 | 2.7254 | 2.0685 | 1.5169 | 2.839 | 2.0685 | 1.5858 | 2.8011 | 1.5141 | 1.379 | 1.5141 | 4.137 | 2.5551 | 3.4475 | 3.1229 | 3.4475 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 30 | 22 | 8 | 0.72 | 30 | 21 | 0.73 | 30 | 24 | 0.72 | 30 | 22 | 0.75 | 30 | 23 | 0.74 | 0.4 | 20 | 0.4 | 60 | 0.675 | 50 | 0.825 | 50
2.4133 | 1.8617 | 0.5516 | 2.7254 | 2.4133 | 1.7927 | 2.8011 | 2.4133 | 1.9306 | 2.7633 | 2.4133 | 1.8617 | 2.9525 | 2.4133 | 1.9306 | 2.9147 | 1.7034 | 1.379 | 1.7034 | 4.137 | 2.5551 | 4.137 | 3.1229 | 4.137 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 35 | 27 | 8 | 0.72 | 35 | 26 | 0.74 | 35 | 28 | 0.73 | 35 | 27 | 0.78 | 35 | 28 | 0.77 | 0.45 | 20 | 0.45 | 60 | 0.675 | 60 | 0.825 | 60
2.758 | 2.2753 | 0.48265 | 2.6876 | 2.758 | 2.1374 | 2.8768 | 2.758 | 2.2753 | 2.8011 | 2.758 | 2.2064 | 3.0282 | 2.758 | 2.2064 | 3.0661 | 1.8926 | 1.379 | 1.8926 | 4.137 | 2.5551 | 4.8265 | 3.1229 | 4.8265 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 40 | 33 | 7 | 0.71 | 40 | 31 | 0.76 | 40 | 33 | 0.74 | 40 | 32 | 0.8 | 40 | 32 | 0.81 | 0.5 | 20 | 0.5 | 60 | 0.675 | 70 | 0.825 | 70
3.1027 | 2.6201 | 0.48265 | 2.6876 | 3.1027 | 2.4822 | 2.9147 | 3.1027 | 2.6201 | 2.839 | 3.1027 | 2.4822 | 3.0661 | 3.1027 | 2.5511 | 3.0661 | 2.0819 | 1.379 | 2.0819 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 45 | 38 | 7 | 0.71 | 45 | 36 | 0.77 | 45 | 38 | 0.75 | 45 | 36 | 0.81 | 45 | 37 | 0.81 | 0.55 | 20 | 0.55 | 60
3.4475 | 2.827 | 0.62055 | 2.6497 | 3.4475 | 2.758 | 2.9904 | 3.4475 | 2.8959 | 2.839 | 3.4475 | 2.827 | 3.0661 | 3.4475 | 2.8959 | 3.0661 | 2.2712 | 1.379 | 2.2712 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 50 | 41 | 9 | 0.7 | 50 | 40 | 0.79 | 50 | 42 | 0.75 | 50 | 41 | 0.81 | 50 | 42 | 0.81 | 0.6 | 20 | 0.6 | 60
3.7923 | 3.1717 | 0.62055 | 2.6876 | 3.7923 | 3.0338 | 3.0282 | 3.7923 | 3.3096 | 2.839 | 3.7923 | 3.1717 | 3.0661 | 3.7923 | 3.1717 | 3.0661 | 2.4604 | 1.379 | 2.4604 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 55 | 46 | 9 | 0.71 | 55 | 44 | 0.8 | 55 | 48 | 0.75 | 55 | 46 | 0.81 | 55 | 46 | 0.81 | 0.65 | 20 | 0.65 | 60
4.137 | 3.4475 | 0.6895 | 2.7254 | 4.137 | 3.3786 | 3.1039 | 4.137 | 3.5854 | 2.839 | 4.137 | 3.5854 | 3.0661 | 4.137 | 3.5164 | 3.0661 | 2.6497 | 1.379 | 2.6497 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 60 | 50 | 10 | 0.72 | 60 | 49 | 0.82 | 60 | 52 | 0.75 | 60 | 52 | 0.81 | 60 | 51 | 0.81 | 0.7 | 20 | 0.7 | 60
[16 empty] | 2.839 | 1.379 | 2.839 | 4.137 | [20 empty] | 3.7853 | 0.06895 | 3.7853 | 0.06895 | [20 empty] | 0.75 | 20 | 0.75 | 60
[16 empty] | 3.0282 | 1.379 | 3.0282 | 4.137 | [20 empty] | 3.7853 | 0.06895 | 3.7853 | 0.06895 | [20 empty] | 0.8 | 20 | 0.8 | 60
[16 empty] | 3.2175 | 1.379 | 3.2175 | 4.137 | [20 empty] | 3.7853 | 0.06895 | 3.7853 | 0.06895 | [20 empty] | 0.85 | 20 | 0.85 | 60

## 38" flow test (2.3 lpm)
total | restrictor R1/T1 | cooling tubes | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10% | total R1/T1 | restrictor R1/T1 | cooling tubes R1/T1 | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10% | total R1/T1 | restrictor R1/T1 | cooling tubes R1/T1 | flow R1/T1 | total R1/T2 | restrictor R1/T2 | G.P.M. R1/T2 | total R2/T1 | restrictor R2/T1 | G.P.M. R2/T1 | min oper PSI | min oper PSI | actual oper PSI | actual oper PSI | rating -10% | rating -10% | rating +10% | rating +10%
0.4137 | 0.2758 | 0.1379 | 0.87062 | 0.4137 | 0.34475 | 1.1356 | 0.4137 | 0.34475 | 1.0599 | 0.75706 | 1.379 | 0.75706 | 4.137 | 2.0441 | 0.6895 | 2.4983 | 0.6895 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 6 | 4 | 2 | 0.23 | 6 | 5 | 0.3 | 6 | 5 | 0.28 | 0.2 | 20 | 0.2 | 60 | 0.54 | 10 | 0.66 | 10
0.48265 | 0.34475 | 0.1379 | 1.022 | 0.6895 | 0.4137 | 1.3627 | 0.6895 | 0.48265 | 1.287 | 0.94632 | 1.379 | 0.94632 | 4.137 | 2.0441 | 1.379 | 2.4983 | 1.379 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 7 | 5 | 2 | 0.27 | 10 | 6 | 0.36 | 10 | 7 | 0.34 | 0.25 | 20 | 0.25 | 60 | 0.54 | 20 | 0.66 | 20
0.51712 | 0.34475 | 0.17238 | 1.0599 | 1.0342 | 0.75845 | 1.5898 | 1.0342 | 0.8274 | 1.5141 | 1.1356 | 1.379 | 1.1356 | 4.137 | 2.0441 | 2.0685 | 2.4983 | 2.0685 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 7.5 | 5 | 2.5 | 0.28 | 15 | 11 | 0.42 | 15 | 12 | 0.4 | 0.3 | 20 | 0.3 | 60 | 0.54 | 30 | 0.66 | 30
0.5516 | 0.4137 | 0.1379 | 1.1356 | 1.379 | 1.1032 | 1.6655 | 1.379 | 1.1032 | 1.6277 | 1.3249 | 1.379 | 1.3249 | 4.137 | 2.0441 | 2.758 | 2.4983 | 2.758 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 8 | 6 | 2 | 0.3 | 20 | 16 | 0.44 | 20 | 16 | 0.43 | 0.35 | 20 | 0.35 | 60 | 0.54 | 40 | 0.66 | 40
0.58608 | 0.4137 | 0.17238 | 1.1734 | 1.7237 | 1.448 | 1.7412 | 1.7237 | 1.448 | 1.7412 | 1.5141 | 1.379 | 1.5141 | 4.137 | 2.0441 | 3.4475 | 2.4983 | 3.4475 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 8.5 | 6 | 2.5 | 0.31 | 25 | 21 | 0.46 | 25 | 21 | 0.46 | 0.4 | 20 | 0.4 | 60 | 0.54 | 50 | 0.66 | 50
0.62055 | 0.4137 | 0.20685 | 1.2113 | 2.0685 | 1.7927 | 1.8169 | 2.0685 | 1.7927 | 1.7412 | 1.7034 | 1.379 | 1.7034 | 4.137 | 2.0441 | 4.137 | 2.4983 | 4.137 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 9 | 6 | 3 | 0.32 | 30 | 26 | 0.48 | 30 | 26 | 0.46 | 0.45 | 20 | 0.45 | 60 | 0.54 | 60 | 0.66 | 60
0.65502 | 0.4137 | 0.24133 | 1.2491 | 2.4133 | 2.1374 | 1.8926 | 2.4133 | 2.1374 | 1.8169 | 1.8926 | 1.379 | 1.8926 | 4.137 | 2.0441 | 4.8265 | 2.4983 | 4.8265 | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 3.7853 | 0.06895 | 9.5 | 6 | 3.5 | 0.33 | 35 | 31 | 0.5 | 35 | 31 | 0.48 | 0.5 | 20 | 0.5 | 60 | 0.54 | 70 | 0.66 | 70
0.6895 | 0.4137 | 0.2758 | 1.287 | 2.758 | 2.4133 | 1.8926 | 2.758 | 2.4822 | 1.8548 | 2.0819 | 1.379 | 2.0819 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 10 | 6 | 4 | 0.34 | 40 | 35 | 0.5 | 40 | 36 | 0.49 | 0.55 | 20 | 0.55 | 60
0.72398 | 0.48265 | 0.24133 | 1.287 | 3.1027 | 2.758 | 1.9684 | 3.1027 | 2.827 | 1.8926 | 2.2712 | 1.379 | 2.2712 | 4.137 |  |  |  |  | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 3.7853 | 0.06895 | 3.7853 | 0.06895 |  |  |  |  | 10.5 | 7 | 3.5 | 0.34 | 45 | 40 | 0.52 | 45 | 41 | 0.5 | 0.6 | 20 | 0.6 | 60
0.75845 | 0.48265 | 0.2758 | 1.3627 | 3.4475 | 3.1027 | 2.0062 | 3.4475 | 3.1027 | 1.8926 | [8 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | [8 empty] | 11 | 7 | 4 | 0.36 | 50 | 45 | 0.53 | 50 | 45 | 0.5
0.79292 | 0.5516 | 0.24133 | 1.4006 | 3.7923 | 3.3786 | 2.0441 | 3.7923 | 3.3786 | 1.8926 | [8 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | [8 empty] | 11.5 | 8 | 3.5 | 0.37 | 55 | 49 | 0.54 | 55 | 49 | 0.5
0.8274 | 0.5516 | 0.2758 | 1.4384 | 4.137 | 3.7923 | 2.0441 | 4.137 | 3.7233 | 1.8926 | [8 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | 0.06895 | 0.06895 | 3.7853 | [8 empty] | 12 | 8 | 4 | 0.38 | 60 | 55 | 0.54 | 60 | 54 | 0.5
0.86187 | 0.62055 | 0.24133 | 1.4384 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 12.5 | 9 | 3.5 | 0.38
0.89635 | 0.62055 | 0.2758 | 1.4763 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 13 | 9 | 4 | 0.39
0.93083 | 0.62055 | 0.31028 | 1.4763 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 13.5 | 9 | 4.5 | 0.39
0.9653 | 0.6895 | 0.2758 | 1.5141 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 14 | 10 | 4 | 0.4
0.99977 | 0.75845 | 0.24133 | 1.5141 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 14.5 | 11 | 3.5 | 0.4
1.0342 | 0.75845 | 0.2758 | 1.552 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 15 | 11 | 4 | 0.41
1.0687 | 0.8274 | 0.24133 | 1.5898 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 15.5 | 12 | 3.5 | 0.42
1.1032 | 0.8274 | 0.2758 | 1.5898 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 16 | 12 | 4 | 0.42
1.1377 | 0.89635 | 0.24133 | 1.5898 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 16.5 | 13 | 3.5 | 0.42
1.1722 | 0.89635 | 0.2758 | 1.6277 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 17 | 13 | 4 | 0.43
1.2066 | 0.9653 | 0.24133 | 1.6277 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 17.5 | 14 | 3.5 | 0.43
1.2411 | 0.9653 | 0.2758 | 1.6655 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 18 | 14 | 4 | 0.44
1.2756 | 1.0342 | 0.24133 | 1.6655 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 18.5 | 15 | 3.5 | 0.44
1.31 | 1.0342 | 0.2758 | 1.6655 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 19 | 15 | 4 | 0.44
1.3445 | 1.1032 | 0.24133 | 1.7034 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 19.5 | 16 | 3.5 | 0.45
1.379 | 1.1032 | 0.2758 | 1.7034 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 20 | 16 | 4 | 0.45
1.4135 | 1.1722 | 0.24133 | 1.7034 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 20.5 | 17 | 3.5 | 0.45
1.448 | 1.1722 | 0.2758 | 1.7412 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 21 | 17 | 4 | 0.46
1.4824 | 1.2411 | 0.24133 | 1.7412 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 21.5 | 18 | 3.5 | 0.46
1.5169 | 1.2411 | 0.2758 | 1.7412 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 22 | 18 | 4 | 0.46
1.5514 | 1.31 | 0.24133 | 1.7412 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 22.5 | 19 | 3.5 | 0.46
1.5858 | 1.31 | 0.2758 | 1.7412 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 23 | 19 | 4 | 0.46
1.6203 | 1.379 | 0.24133 | 1.7791 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 23.5 | 20 | 3.5 | 0.47
1.6548 | 1.379 | 0.2758 | 1.7791 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 24 | 20 | 4 | 0.47
1.6893 | 1.448 | 0.24133 | 1.7791 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 24.5 | 21 | 3.5 | 0.47
1.7237 | 1.448 | 0.2758 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 25 | 21 | 4 | 0.48
1.7582 | 1.5169 | 0.24133 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 25.5 | 22 | 3.5 | 0.48
1.7927 | 1.5169 | 0.2758 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 26 | 22 | 4 | 0.48
1.8272 | 1.5858 | 0.24133 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 26.5 | 23 | 3.5 | 0.48
1.8617 | 1.6548 | 0.20685 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 27 | 24 | 3 | 0.48
1.8961 | 1.6548 | 0.24133 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 27.5 | 24 | 3.5 | 0.48
1.9306 | 1.6548 | 0.2758 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 28 | 24 | 4 | 0.48
1.9651 | 1.7237 | 0.24133 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 28.5 | 25 | 3.5 | 0.48
1.9995 | 1.7237 | 0.2758 | 1.8169 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 29 | 25 | 4 | 0.48
2.034 | 1.7927 | 0.24133 | 1.8548 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 29.5 | 26 | 3.5 | 0.49
2.0685 | 1.7927 | 0.2758 | 1.8548 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 30 | 26 | 4 | 0.49
2.103 | 1.8617 | 0.24133 | 1.8548 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 30.5 | 27 | 3.5 | 0.49
2.1719 | 1.9306 | 0.24133 | 1.8548 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 31.5 | 28 | 3.5 | 0.49
2.2064 | 1.9306 | 0.2758 | 1.8548 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 32 | 28 | 4 | 0.49
2.2409 | 1.9306 | 0.31028 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 32.5 | 28 | 4.5 | 0.5
2.2753 | 1.9995 | 0.2758 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 33 | 29 | 4 | 0.5
2.3098 | 2.0685 | 0.24133 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 33.5 | 30 | 3.5 | 0.5
2.3443 | 2.0685 | 0.2758 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 34 | 30 | 4 | 0.5
2.3788 | 2.1374 | 0.24133 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 34.5 | 31 | 3.5 | 0.5
2.4133 | 2.1374 | 0.2758 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 35 | 31 | 4 | 0.5
2.4477 | 2.2064 | 0.24133 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 35.5 | 32 | 3.5 | 0.5
2.4822 | 2.2064 | 0.2758 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 36 | 32 | 4 | 0.5
2.5167 | 2.2064 | 0.31028 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 36.5 | 32 | 4.5 | 0.5
2.5856 | 2.2753 | 0.31028 | 1.8926 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 37.5 | 33 | 4.5 | 0.5
2.6201 | 2.3443 | 0.2758 | 1.9305 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 38 | 34 | 4 | 0.51
2.6546 | 2.3443 | 0.31028 | 1.9305 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 38.5 | 34 | 4.5 | 0.51
2.689 | 2.4133 | 0.2758 | 1.9305 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 39 | 35 | 4 | 0.51
2.7235 | 2.4133 | 0.31028 | 1.9305 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 39.5 | 35 | 4.5 | 0.51
2.758 | 2.4822 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 40 | 36 | 4 | 0.52
2.7925 | 2.4822 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 40.5 | 36 | 4.5 | 0.52
2.827 | 2.5511 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 41 | 37 | 4 | 0.52
2.8614 | 2.5511 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 41.5 | 37 | 4.5 | 0.52
2.8959 | 2.6201 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 42 | 38 | 4 | 0.52
2.9304 | 2.6201 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 42.5 | 38 | 4.5 | 0.52
2.9649 | 2.689 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 43 | 39 | 4 | 0.52
2.9993 | 2.689 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 43.5 | 39 | 4.5 | 0.52
3.0338 | 2.758 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 44 | 40 | 4 | 0.52
3.0683 | 2.758 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 44.5 | 40 | 4.5 | 0.52
3.1027 | 2.827 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 45 | 41 | 4 | 0.52
3.1372 | 2.827 | 0.31028 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 45.5 | 41 | 4.5 | 0.52
3.1717 | 2.8959 | 0.2758 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 46 | 42 | 4 | 0.52
3.3096 | 2.9649 | 0.34475 | 1.9684 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 48 | 43 | 5 | 0.52
3.4475 | 3.1027 | 0.34475 | 2.0062 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 50 | 45 | 5 | 0.53
3.5854 | 3.2407 | 0.34475 | 2.0062 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 52 | 47 | 5 | 0.53
3.7233 | 3.3786 | 0.34475 | 2.0062 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 54 | 49 | 5 | 0.53
3.8612 | 3.5164 | 0.34475 | 2.0441 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 56 | 51 | 5 | 0.54
3.9991 | 3.6543 | 0.34475 | 2.0441 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 58 | 53 | 5 | 0.54
4.137 | 3.7923 | 0.34475 | 2.0819 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 60 | 55 | 5 | 0.55
4.2749 | 3.8612 | 0.4137 | 2.0819 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 62 | 56 | 6 | 0.55
4.4128 | 4.0681 | 0.34475 | 2.0819 | [14 empty] | 0.06895 | 0.06895 | 0.06895 | 3.7853 | [14 empty] | 64 | 59 | 5 | 0.55

## fitting list ye1
CSC Cooling Circuit ME1/2
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-4-6B 1/4" MPT to 3/8" hose barb | Brass
E | Parker # 821-6 3/8" Push lok hose | MSHA approved
F | Parker # 30382-6-6B 3/8" male 37 deg to barb | Brass
F | Parker # 6 BTX B Nut | Brass
F | Parker # 6 TX B Sleeve | Brass
3/8" copper tube
F,E
D | Parker # 3JC82-6-6B/C (barb to female O-ring) | Brass
G | Parker # 3J082-6-6B/C (Barb to male O-ring) | Brass
E,F
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F,3/8" copper tube,F,E,C
L | Hayes Mesurflo # 2305-00061- 1/4" IPS flow regulator (0.6 GPM) | Bronze
M | Parker # 216P-6 3/8" hex nipple | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
CSC Cooling Circuit ME1/3
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-4-6B 1/4" MPT to 3/8" hose barb | Brass
E | Parker # 821-6 3/8" Push lok hose | MSHA approved
D | Parker # 3JC82-6-6B/C (barb to female O-ring) | Brass
G | Parker # 3J082-6-6B/C (Barb to male O-ring) | Brass
E
F | Parker # 30382-6-6B 3/8" male 37 deg to barb | Brass
F | Parker # 6 BTX B Nut
F | Parker # 6 TX B Sleeve | Brass
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,C
L | Hayes Mesurflo # 2305-00061- 1/4" IPS flow regulator (0.6 GPM) | Bronze
M | Parker # 216P-6 3/8" hex nipple | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
Disk Cooling Circuit
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze/SS
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-6-8B 3/8" MPT to barb | Brass
E | Parker # 821-8 1/2" push lok hose | MSHA approved
F | Parker # 30482-8-8B 1/2" Male 45 deg to barb | Brass
F | Parker # 8 TX-BB nut | Brass
F | Parker # 8 TX-BB sleeve | Brass
| Corner plate / Cooling tube assembly | Copper
F,E,F
| Corner plate / Cooling tube assembly | Copper
F,E,C
L | Hayes Mesurflo # 2305-1021 - 3/8" IPS flow regulator (0.5 GPM) | Bronze
M | Parker # 216-6 3/8" Hex nipple - brass | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze/SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
VME rack loop (6/9 per disk) Figure 5
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-6-8B 3/8" MPT to barb | Brass
E | Parker # 821-8 1/2" push lok hose | MSHA approved
F | Parker # 30382-6-8B 3/8" male 37 deg to 1/2" barb | Brass
F | Parker # 6BTX-BB nut | Brass
F | Parker # 6TX-BB sleeve | Brass
Transformer,F,E,F
Transformer,F,E,F
Transformer,F,E,F
Transformer,F,E,F
VME Rack,F,E,F
Transformer,F,E,F
Transformer,F,E,C
L | Hayes Mesurflo # 2305-1091 flow regulator (2.5 GPM) | Bronze
M | Parker # 216-6 3/8" Hex nipple - brass | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
RPC cooling loop (18? per station 3, 18? Per station 1)
Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold)
weld half-couplings to manifold
HE cooling loop (18? per station 1)
Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold)
weld half-couplings to manifold

## fitting list
CSC Cooling Circuit ME2,3/1
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-4-6B 1/4" MPT to 3/8" hose barb | Brass
E | Parker # 821-6 3/8" Push lok hose | MSHA approved
F | Parker # 30382-6-6B 3/8" male 37 deg to barb | Brass
F | Parker # 6 BTX B Nut | Brass
F | Parker # 6 TX B Sleeve | Brass
I | 3/8" copper tube
F,E
D | Parker # 3JC82-6-6B (barb to female O-ring) | Brass
G | Parker # 3J082-6-6B (Barb to male O-ring) | Brass
E,F
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F,I,F,E,C
L | Hayes Mesurflo # 2305-0061- 1/4" IPS flow regulator (0.6 GPM) | Bronze
M | Parker # 216P-4 1/4" hex nipple | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
CSC Cooling Circuit ME2,3/2
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-4-6B 1/4" MPT to 3/8" hose barb | Brass
E | Parker # 821-6 3/8" Push lok hose | MSHA approved
D | Parker # 3JC82-6-6B (barb to female O-ring) | Brass
G | Parker # 3J082-6-6B (Barb to male O-ring) | Brass
E
F | Parker # 30382-6-6B 3/8" male 37 deg to barb | Brass
F | Parker # 6 BTX B Nut
F | Parker # 6 TX B Sleeve | Brass
| Chamber (3/8" OD X .032 wall copper tube) | Brass
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,F
| Chamber (3/8" OD X .032 wall copper tube) | Copper
F,E,D,G,E,C
L | Hayes Mesurflo # 2305-0061- 1/4" IPS flow regulator (0.6 GPM) | Bronze
M | Parker # 216P-4 1/4" hex nipple | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 7B-841-01 1/4" Ball valve w/ SS ball & stem & side port | Bronze
N | Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
Disk Cooling Circuit
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze/SS
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-6-8B 3/8" MPT to barb | Brass
E | Parker # 821-8 1/2" push lok hose | MSHA approved
F | Parker # 30482-8-8B 1/2" Male 45 deg to barb | Brass
F | Parker # 8 TX-BB nut | Brass
F | Parker # 8 TX-BB sleeve | Brass
| Corner plate / Cooling tube assembly | Copper
F,E,F
| Corner plate / Cooling tube assembly | Copper
F,E,C
L | Hayes Mesurflo # 2305-1021 - 3/8" IPS flow regulator (0.5 GPM) | Bronze
M | Parker # 216-6 3/8" Hex nipple - brass | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze/SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
VME rack loop (6/9 per disk) Figure 5
KEY | Description | Material
| 1.5" sch 5 SS supply manifold | 304 SS
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
C | Parker # 30182-6-8B 3/8" MPT to barb | Brass
E | Parker # 821-8 1/2" push lok hose | MSHA approved
F | Parker # 30382-6-8B 3/8" male 37 deg to 1/2" barb | Brass
F | Parker # 6BTX-BB nut | Brass
F | Parker # 6TX-BB sleeve | Brass
Transformer,F,E,F
Transformer,F,E,F
Transformer,F,E,F
Transformer,F,E,F
VME Rack,F,E,F
Transformer,F,E,F
Transformer,F,E,C
L | Hayes Mesurflo # 2305-1091 flow regulator (2.5 GPM) | Bronze
M | Parker # 216-6 3/8" Hex nipple - brass | Brass
B | B&G # RP-250B Bell & Gossett Readout Valve | Brass
A | Apollo # 70-843-07 ball valve 3/8" w/SS ball & stem | Bronze
N | Ladish # 32915 half coupling 3/8" pipe thread (welded to manifold) | 316 SS
| 1.5" sch 5 SS return manifold | 304 SS
RPC cooling loop (18? per station 3, 18? Per station 1)
Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold)
weld half-couplings to manifold
HE cooling loop (18? per station 1)
Ladish # 32915 half coupling 1/4" pipe thread (welded to manifold)
weld half-couplings to manifold

## Flow summary
Flow summary
Periphery manifolds | Units
Total flow per endcap | liter/min | 671
Total Heat removed per endcap | W | 71134
Total temperature rise | C | 1.5217
Tower manifolds | Units
Total flow per endcap | liter/min | 182.4
Total Heat removed per endcap | W | 28200
Total temperature rise | C | 2.2192
For both manifolds | Units
Total flow per endcap | liter/min | 853.4
Total Heat removed per endcap | W | 99334
Total temperature rise | C | 1.6708

## YE1 Flow calculations
YE1 cooling parameters
| Units | YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 1586.8003 | 585.0526 | 1586.8003 | 585.0526
Flow rate | liter/min | 332.8 | 2.3 | 2.3 | 2.3 | 2 | 2 | 2 | 2 | 5 | 2 | 4 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.1732 | 0.76683 | 0.76683 | 0.76683 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 119727.7574 | 5912.3984 | 5912.3984 | 5912.3984 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/circuit | W | 28620 | 344 | 420 | 200 | 72 | 72 | 182 | 80 | 852 | 400 | 247 | 147 | 390 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.2344 | 2.1469 | 2.6212 | 1.2482 | 0.51675 | 0.51675 | 1.3062 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 18 | 18 | 6 | 12 | 6 | 30 | 4 | 1 | 8 | 1 | 8
Total flow | lt/min | 332.8 | 20.7 | 20.7 | 41.4 | 12 | 12 | 36 | 36 | 30 | 24 | 24 | 60 | 16 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 28620 | 3096 | 3780 | 3600 | 432 | 432 | 3276 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [9 empty] | 4800
Pressure drop (measured) | bar | [6 empty] | 1.6? |  | 10.5psi/lvps
Total flow-disk manifold | liter/min | 332.8
Total Heat removed | W | 28620
Total temperature rise | C | 1.2344
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192

## YE2 Flow calculations
YE2 cooling parameters
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 176.8 | 2.3 | 2.3 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.857 | 0.78256 | 0.78256 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 80666.7762 | 5972.7244 | 5972.7244 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/circuit | W | 27032 | 327 | 390 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.1947 | 2.0408 | 2.434 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 176.8 | 55.2 | 27.6 | 24 | 20 | 10 | 40
Heat removed | W | 27032 | 7848 | 4680 |  | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 4800
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
Total flow | liter/min | 176.8
Total Heat removed | W | 27032
Total temperature rise | C | 2.1947

## YE3 Flow calculations
YE3 cooling parameters
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 161.4 | 2.3 | 2.3 | 2 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.6952 | 0.78256 | 0.78256 | 1.1795 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 73640.3715 | 5972.7244 | 5972.7244 | 6837.8172 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/circuit | W | 15482 | 360 | 369 | 80 | 400 | 426 | 193 | 2516
Temperature rise | C | 1.3769 | 2.2467 | 2.3029 | 0.57416 | 2.8708 | 1.223 | 0.55407 | 3.6115
Number of circuits | ea | 1 | 12 | 6 | 18 | 12 | 4 | 4 | 2
Total flow | liter/min | 161.4 | 27.6 | 13.8 | 36 | 24 | 20 | 20 | 20
Heat removed | W | 15482 | 4320 | 2214 | 1440 |  | 1704 | 772 | 5032
Heat removal capacity | W |  |  |  |  | 4800
Pressure drop (measured) | bar
Total flow | liter/min | 161.4
Total Heat removed | W | 15482
Total temperature rise | C | 1.3769

## Static pressure tests
Hour | psi | Hour | Bar
0 | 287 | 0 | 19.7931
3 | 277 | 3 | 19.1034
19.5 | 203 | 19.5 | 14
21 | 203 | 21 | 14
24 | 205 | 24 | 14.1379
27 | 205 | 27 | 14.1379
42.5 | 185 | 42.5 | 12.7586
47.5 | 185 | 47.5 | 12.7586
50.5 | 200 | 50.5 | 13.7931
114.5 | 180 | 114.5 | 12.4138
117.5 | 182 | 117.5 | 12.5517
119.5 | 307 | 119.5 | 21.1724
138.5 | 255 | 138.5 | 17.5862
146.5 | 258 | 146.5 | 17.7931
163.5 | 238 | 163.5 | 16.4138
166.5 | 305 | 166.5 | 21.0345
187 | 245 | 187 | 16.8966
211 | 225 | 211 | 15.5172
215 | 243 | 215 | 16.7586
218.5 | 310 | 218.5 | 21.3793
234.5 | 232 | 234.5 | 16
243 | 250 | 243 | 17.2414
259 | 232 | 259 | 16

## Flow tests
Test No.
3 | Only 0.6 gpm (2.3 lpm) restrictor
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.49 | 1.3793 | 1.862
| 25 | 0.51 | 1.7241 | 1.938
| 30 | 0.54 | 2.069 | 2.052
| 35 | 0.55 | 2.4138 | 2.09
| 40 | 0.56 | 2.7586 | 2.128
| 45 | 0.58 | 3.1034 | 2.204
| 50 | 0.59 | 3.4483 | 2.242
| 55 | 0.6 | 3.7931 | 2.28
| 60 | 0.62 | 4.1379 | 2.356
4 | Full System 0.6 gpm (2.3 lpm) restrictor
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.26 | 1.3793 | 0.988
| 25 | 0.3 | 1.7241 | 1.14
| 30 | 0.36 | 2.069 | 1.368
| 35 | 0.39 | 2.4138 | 1.482
| 40 | 0.42 | 2.7586 | 1.596
| 45 | 0.46 | 3.1034 | 1.748
| 50 | 0.48 | 3.4483 | 1.824
| 55 | 0.5 | 3.7931 | 1.9
| 60 | 0.52 | 4.1379 | 1.976
9 | Full System 0.75gpm (2.85 lpm) restrictor
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.25 | 1.3793 | 0.95
| 25 | 0.33 | 1.7241 | 1.254
| 30 | 0.38 | 2.069 | 1.444
| 35 | 0.42 | 2.4138 | 1.596
| 40 | 0.46 | 2.7586 | 1.748
| 45 | 0.5 | 3.1034 | 1.9
| 50 | 0.52 | 3.4483 | 1.976
| 55 | 0.56 | 3.7931 | 2.128
| 60 | 0.59 | 4.1379 | 2.242
10 | Full System with no restrictor
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.29 | 1.3793 | 1.102
| 25 | 0.35 | 1.7241 | 1.33
| 30 | 0.39 | 2.069 | 1.482
| 35 | 0.44 | 2.4138 | 1.672
| 40 | 0.48 | 2.7586 | 1.824
| 45 | 0.52 | 3.1034 | 1.976
| 50 | 0.54 | 3.4483 | 2.052
| 55 | 0.58 | 3.7931 | 2.204
| 60 | 0.62 | 4.1379 | 2.356
11 | One copper cooling loop only
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.62 | 1.3793 | 2.356
| 25 | 0.7 | 1.7241 | 2.66
| 30 | 0.78 | 2.069 | 2.964
| 35 | 0.86 | 2.4138 | 3.268
| 40 | 0.92 | 2.7586 | 3.496
| 45 | 0.98 | 3.1034 | 3.724
| 50 | 1.06 | 3.4483 | 4.028
| 55 | 1.1 | 3.7931 | 4.18
| 60 | 1.16 | 4.1379 | 4.408
12 | Full System 0.6 gpm (2.3 lpm) restrictor replace hose with tube
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.29 | 1.3793 | 1.102
| 25 | 0.34 | 1.7241 | 1.292
| 30 | 0.38 | 2.069 | 1.444
| 35 | 0.44 | 2.4138 | 1.672
| 40 | 0.48 | 2.7586 | 1.824
| 45 | 0.51 | 3.1034 | 1.938
| 50 | 0.55 | 3.4483 | 2.09
| 55 | 0.58 | 3.7931 | 2.204
| 60 | 0.63 | 4.1379 | 2.394
13 | One aluminum cooling loop only
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 20 | 0.5 | 1.3793 | 1.9
| 25 | 0.57 | 1.7241 | 2.166
| 30 | 0.64 | 2.069 | 2.432
| 35 | 0.7 | 2.4138 | 2.66
| 40 | 0.76 | 2.7586 | 2.888
| 45 | 0.81 | 3.1034 | 3.078
| 50 | 0.86 | 3.4483 | 3.268
| 55 | 0.92 | 3.7931 | 3.496
| 60 | 0.97 | 4.1379 | 3.686
14 | One 3/8" copper cooling loop only per new design
| Pressure Drop (psi) | Flow (gpm) | Pressure Drop (bar) | Flow (lpm)
| 0.5 | 0.84 | 0.034483 | 3.192
| 1 | 0.93 | 0.068966 | 3.534
| 2 | 1.05 | 0.13793 | 3.99
| 3 | 1.25 | 0.2069 | 4.75
| 4 | 1.38 | 0.27586 | 5.244
| 5 | 1.52 | 0.34483 | 5.776
| 6 | 1.64 | 0.41379 | 6.232
| 7 | 1.75 | 0.48276 | 6.65
| 8 | 1.86 | 0.55172 | 7.068