## Slide 1: Ambient condition P5 specifically Humidity
Ian
06 July 2015

## Slide 2: RH in UXC55 since 2010
3 periods 2010, 2011 and 2012 stable upper RH limits
43% RH

## Slide 3: RH UXC55 alignment sensor X3 minus
From the dew point and Temp the RH can be calculated.
DP 8.5degC = 49% RH

## Slide 4: Temperature UXC55
19.8degC

## Slide 5
Previous to 2011 temp UXC was not stable, there was some training period
Unfortunately for RH there are no records available before 2010
Since Jan 2015 for both Temp and RH there may be a similar training period ?

## Slide 6: RH RE+1 4 positions 2010 to date
High RH reading 46%
Low RH reading 41%

## Slide 7: RH RE+2 4 positions 2010 to date
RH 45%

## Slide 8: RH RE+3 4 positions 2010 to date
RH 45%

## Slide 9: Temperature of cooling system RE+1

## Slide 10: RH RE-1 4 positions 2010 to date
RH average upper limit 47%

## Slide 11: RH RE-2 4 positions 2010 to date
RH average upper limit 47%

## Slide 12: RH RE-3 4 positions 2010 to date
RH average upper limit 45%

## Slide 13
UXC55
RE+1
RE+2
RE+3
RE-1
The Disk Sensors show similar increase since Jan 2015 to the UXC55 sensor. Nota the ordinate is scale variant, abscissa almost not.
RE-3
RE-2

## Slide 14: RH since 2010
All values available from UXC and REs agree to within ± 4% RH.
Response to changing values is also similar.

## Slide 15: Values of RH taken at time XXXX for UXC and Disks (REs)
Intend to show that sensors agree, or not, at instantaneous times rather than spanned out over years.

## Slide 16: Average Current in RE back to 2010

## Slide 17: Temp in RE log of data is not available here.

## Slide 18: RH in Barrel region WM2 BIN (others are Bout, Tin and Tout, not shown
As these are marked in and out then is this RH gas or RH ambient ?

## Slide 19: Temp taken from WM2 of S10 RB4minus BUT it shows RB1,2,3 and 4…….

## Slide 20: Temperatures in RB global

## Slide 21: Currents, average in RB since 2010

## Slide 23
There may be 8% dispersion in the RH readings in RE and UXC.
No data from the RE4s
Years 2010, 2011 and 2012 were more stable than 2015 as shown by the sensors on the disk faces.
RH in RB is not clear if gas or Ambient. ?
It is clear that RH values for 2015 are not yet stable, with excursions higher than the stable upper limit from 2010, 2011 & 2012.