HALOGEN FREE, LOW SMOKE FLAME RETARDAT DATA CABLE ACCORDING TO IS23 CERN

CONSTRUCTION DETAILS

Conductor     	: 	nomin. sect.   0.08 mm2, 7x0,127 mm tinned copper

cond. diam. 0.39 mm

Insulation    	: 	High density polyethylene LSZH, nominal thickness 0,19 mm

nominal diameter   0.77 mm +/-0,01 mm

Pairs     	:  	each group of 4 pairs white/blue white/orange white/green

white/brown

nominal diameter   1.54 mm

Lay up      	: 	pairs twisted in 5 groups of 4 pairs

diameter over assembly 3.10 mm

Identification  	: 	numbered polyester tape on each group

Assembly      	: 	groups twisted together with suitable LSZH fillers

diameter over assembly            7.05 mm

Overall Shield	: 	aluminium/polyester tape as flame barrier

tinned copper braid wire diameter 0.10 mm nominal coverage 85%

nominal diameter 7.60 mm

Outer sheath   	: 	Thermoplastic LSZH flame retardant compound

colour BLUE RAL 5015

nominal thickness 1.10 mm

nominal diameter  9.8 mm, 10.0 mm Max.

------------------------------------------------------------

ELECTRICAL AND PHYSICAL CHARACTERISTICS

Electrical resistance sect.  AWG 28 < 222 ohm/km at 20°C

Insulation resistance    >   1000 Mohm x km at 20° C

Impedance :				110 OHM +/-10%

Max. working voltage      	:   150  V

Skew time between pairs on 25 m < 2ns

OTHER CHARACTERISTICS

Weight :  142 kg/km

Bending radius static min.          :   65 mm

Working temperature range static : from -30 to +70 °C

REFERENCE STANDARDS

IEC 60332-1, CERN IS23(excluding radiation resistance of the outer sheath)