## Slide 1: LS2 Electrical Services Upgrade: HB
S. Lusin

## Slide 2: HB Power Cabling: YB0 Run3 Configuration
Add 4 Maratons per side during LS2
Leave 1 A3486 & 1 EASY 3000 crate per side to support HO
Remove 1 EASY 3000 crate per side during LS2
Power requirements for HB expected to double in Run 3
Will need 2 new power cables
+ 1 power distribution box per side

## Slide 3: LV Distribution Boxes
Boxes will be prepared & installed in HB racks by TC electrical team
Outputs of Maraton-type distribution boxes consist of short cables anchored by strain relief
HCAL team will prepare & connectorize output cables, provide them to TC electrical team prior to distribution box installation
HCAL will decide where boxes are to be installed & how output cables are to be routed

## Slide 4: S4F Zone
Will need 4 new circuit breakers in armoire EXD20/55
Will need 4 new USC-UXC power cables installed
Need 2 (4) new armoire-rack power cables installed
Two OPFC crates to be installed in racks S4F06-S4F07
8 HB OPFCs located in 2 OPFC crates in S4F racks
Provide 385 VDC to Maratons in UXC

## Slide 5: S4F Zone: Distribution Borniers at Rear of OPFC Crates
Need 2 such borniers, best installed in OPFC crate prior to installation in rack