## Slide 1: LS2 Electrical Services Upgrade: ME
S. Lusin

## Slide 2: ME Power & DCS Cabling: YE+2 Run2 & Run3 Configurations
… for which CSC group plans to add 2 Maratons per tower
No new USC-UXC power cabling will be required …
Currently 8 Maratons/side
… serving both ME2 & ME3
DCFEBs for upgraded ME2/1 & ME3/1 will require increased power
Will use spare pair of conductors in each of existing 7x6 power cables
Power cables are already routed to the appropriate OPFC rack in S4F zone of USC
Will need to add power “jumper” cable in each YE2 tower
… and modify 4 existing LV distribution boxes on each YE2 disk
Run 2
Run 3

## Slide 3: ME Power & DCS Cabling: YE+3 Run2 & Run3 Configurations
Again, will use spare conductor pair in each power cable, so no new USC-UXC cabling required
Configuration is equivalent to ½ of YE2
Will need to add two new LV distribution boxes in order to split RE & ME
YE3 similar …
Currently 2 Maratons per YE3 tower
CSC group will add 1 Maraton per tower
Run 2
Run 3

## Slide 4: ME Power & DCS Cabling: Alternative YE2 Run3 Configuration
Simpler to realize, but will have consequences for DSS action matrix
… and long output cables to connect to X3 level
X2 & X4 racks are unchanged
Referred to as “symmetric” configuration
All new Maratons are placed in X3 racks
In this case, no “power jumper cable” is needed
Will need different design of LV distribution boxes

## Slide 5: ME Power & DCS Cabling: YE-2 Run2 & Run3 Configurations
for reference ...
Run 2
Run 3

## Slide 6: ME Power & DCS Cabling: YE-3 Run2 & Run3 Configurations
Run 2
Run 3
for reference ...

## Slide 7: LV Distribution Boxes: Plus End asym
YE+2 Far Side
YE+2 Near Side
YE+3
X4
X2

## Slide 8: LV Distribution Boxes: Minus End asym
YE-2 Far Side
YE-2 Near Side
YE-3
X4
X2
for reference ...

## Slide 9: LV Distribution Boxes: Plus End sym
YE+2 Far Side
YE-2 Near Side
X4
X2
for reference ...

## Slide 10: LV Distribution Boxes: Minus End sym
YE-2 Far Side
YE-2 Near Side
X4
X2
for reference ...

## Slide 11: OPFC Crates in S4: Run 2 Configuration
Added 2 OPFC bins during LS1 as result of increased power requirements of upgraded ME1/1 chambers
Input cables from electrical armoires in S4
Output cables to UXC racks
Output cables to UXC racks
No new cabling to UXC was required
Used spare conductor pairs in existing cables
Used in-rack “jumpers” to connect new OPFCs to target conductor pairs

## Slide 12: OPFC Crates in S4: Run 3 Configuration
Jumpers connect to borniers used to terminate USC-UXC power cables
Will need to add 2 more OPFC bins during LS2 to power upgraded ME2/1, 3/1 & 4/1 chambers
Will make room for these bins by finding alternative home for CSC DCS power supplies
Again, no new cabling to UXC is required
Borniers arranged to power 3 groups of 2 OPFCs in each bin
Again, in-rack “jumpers” connect new OPFCs to target conductor pairs

## Slide 13: Power Patch Panels: RE Power, Service Power & DCS
Two of these required
Instead of jacketed cable, outputs routed via in-rack jumper wires

## Slide 14: S4F Zone Tasks for ME
Six new circuit breakers to install in armoire EXD20/55
Two OPFC power bins to install, with custom borniers
Power jumper wiring to install between new OPFCs and existing 7x6 power cabling
Three new armoire-to-rack power cables to install