## Slide 1: Cooling circuit constraint , Delta “P”
Ian Crotty 30 Oct 2014

## Slide 2: Choice of 6mm or 8mm dia Cu piping
Chart: Dellta P "v" Flow Rate
| 1 | 2 | 3 | 4 | 5 | 7.5 | 10
Delta P "v" Flow Rate for dia 6-8mm | 133 | 461 | 969 | 1658 | 2522 | 5455 | 9486
Delta P "v" Flow Rate 4-6mm | 281.6 | 977 | 3526 | 7600 | 13189 | 20291 | 44661 | 78477

## Slide 3: Conclusion
The pressure drop over 20deg is in the order of 1 bar @ 2l/min with 8mm pipe without any unions or bends.
The pressure drop over 20deg is in the order of 8 bar @ 2l/min with 6mm pipe without any unions or bends
Clearly we need to use 6-8mm pipe.