## Slide 1: Endcap Chambers temperatures Monitoring
Ian, Andrea, Gabriella

## Slide 2: Analysis and outlook
Monitoring over 2018 (May-Dec): we selected one chamber for each ring and station.
Temperature distribution on the disk: we map the temperature chamber by chamber for one day
Comparison FOS and PT100 sensors
Conclusion
Note: the error that is not showed in the plots is 0.2 degres

## Slide 3
YE4
YE3
YE2
RE4 chambers are attached to the CSC
RE3 chambers are attached to the YE3
RE1 & RE2 chambers are attached to the YE1
YE1

## Slide 4: RPC cooling circuit
Chamber cooling:
RE1: double lines of copper pipes
RE2 and RE3: single line of copper pipe
RE4: double lines of copper pipes and bigger copper plates
RE2-RE3-RE4:
One cooling channel supplies 4 chambers connected in series: two chambers (one odd and one even) for each ring.
RE1: 6 chambers in series
Sensors:
PT-100 is located inside the chamber (one out of 6 chamber)
FOS Temperature sensors are located at the edge of the chamber (one per chamber)
RE1
RE4
RE2 and RE3

## Slide 5
Ring 2
Ring 3
Cavern Temperature
DISK4
18.6 ÷ 19.0
18.2 ÷ 17.4
FOS CH1
19.2
19.9

## Slide 6
Ring 2
Ring 3
DISK3
Cavern Temperature
20.6 ÷ 20.2
19.8 ÷ 19.0
FOS CH1
19.2
19.9

## Slide 7
Ring 2
Ring 3
DISK2
19.9 ÷ 19.2
19.7 ÷ 18.8
Cavern Temperature
FOS CH1

## Slide 8
Monitoring of chamber # 1 in 2018
DISK-2
19.8 ÷ 19.2
19.6 ÷ 18.9
Ring 2
Ring 3

## Slide 9
ring3
Monitoring of chamber # 1 in 2018
20.2 ÷ 19.3
20.2 ÷ 18.8
DISK-3
ring2

## Slide 10
Monitoring of chamber # 1 in 2018
17.8 ÷ 18.8
DISK-4

## Slide 11: Summary table and conclusion (1)
 | RE4 | RE3 | RE2 | RE-2 | RE-3 | RE-4
Ring 2 | 0.40 18.6-19.00 | 0.50 20.7-20.20 | 0.60 19.8-19.20 | 0.60 19.5-18.90 | 0.40 19.7-20.10 | 0.50 18.5-18.00
Ring 3 | 0.90 18.2-17.30 | 0.60 19.8-19.20 | 0.80 19.7-18.90 | 0.80 19.9-19.10 | 0.40 20.2-17.80 | 0.30 18.7-18.40
Maximum temperature variation over the year is 0.9 degrees
RE4+ and RE4- have lowest temperature
RE4- has a smaller variation because of the shaft
For all disks, the Ring 3 temperature has bigger variation. It could be due to the cavern temperature variations

## Slide 12
RE4
18.0
18.6
18.8
18.6
10.0
18.6
19.0
18.6
18.7
18.4
18.5
18.6
18
18.9
18.3
18.3
18.5
18.3
18.8
18.6
18.4
18.6
18.6
18.4
18.8
18.4
19
18.5
18.7
18.8
18.5
18.2
18.3
 | Average | 
Ring 2 | 18.50 | 18.50
Ring 3 | 18.40 | 
Odd |  | 18.40
Even |  | 18.40
Upper Half | 18.6 | 18.5
 | 18.4 | 
Lower Half | 18.5 | 18.4
 | 18.4 | 
18.1
20.0
18.4
17.9
17.8
18.2
21.2
17.8
17.9
19
18.0
18.3
18.1
18.4
18.4
18.6
18.5
18.8
18.7
18.5
18.7
18.4
18.3
18.1
16.2
16.9
18.6
18.4
18
18.1
17.3
18.3
18.9
18.6
19.8
18.1
18.4
18.5
18.7
Temperature @ August 1st
RE4
No significant dependence by chamber position with respect to the CSC position (on yoke – off yoke) and low half and upper half of the RPCs.

## Slide 13
RE+3
20.9
19.5
19.3
19.0
19.0
19.6
21.7
21.0
19.5
21.3
20.1
20.3
19.2
19.4
20,2
20
19.5
18.9
19.1
19.2
19.5
19.1
19.6
20.3
20.1
20.3
20.1
19.8
20.2
19
20.1
19.2
19.6
20.3
20.0
19.6
19.1
18.5
19.8
19.7
19.8
19.9
20.0
23.6
19.3
19.1
19.9
20.1
19.3
16.8
23.7
17.2
17.9
21.1
21.2
18.8
18.5
18.5
18.5
19.8
19.9
19.1
18.7
19.1
21.6
20.9
18.3
18.9
18.4
18.5
19.5
18.5
 | Average | 
Ring 2 | 19.80 | 19.70
Ring 3 | 19.60 | 
Odd |  | 19.50
Even |  | 19.90
Upper Half |  | 20.00
Lower Half |  | 19.30
RE+3
No significant dependence by chamber position with respect to the CSC position (on yoke – off yoke)
Lower half chambers with 1 degrees less then the upper half station

## Slide 14: Comparison between FOS and PT100 sensors
 | RE4 | RE3 | RE2 | RE1 | RE-1 | RE-2 | RE-3 | RE-4
FOS | 18.20 | 19.50 | 19.60 |  |  | 18.70 | 19.80 | 17.80
PT100 |  | 20.90 | 20.10 | 20.80 | 20.60 | 21.00 | 21.70 | 
Approximately 2 degrees difference between FOS-PT100
The RE1 temperature is similar to the stations RE2 and RE3 despite having double copper pipe layout, 6 chambers in series and lower convection air
In RE1 station only PT sensors are installed

## Slide 15: Conclusion
The present CMS cooling system is capable of maintaining stable temperature in the optimal range for longevity and stable performance of the RPCs
The improved RE4 circuit has proved to be more effective then the other stations (lower temperature and more stable).
The cooling circuit on the Yoke is fundamental to keeping stable and low the temperature on the four RPC stations.

## Slide 16: SPARE

## Slide 17
RE-2/ring2
RE-2/ring3

## Slide 18
EP4
18
Ring 2
Ring 3

## Slide 19
EP3
19
Ring 2
Ring 3

## Slide 20
EP2
Ring 2
Ring 3

## Slide 21
EP4
21
Ring 2
Ring 3

## Slide 22
EP3
Ring 3
Ring 2

## Slide 23
EN4
23
Ring 3
Ring 2

## Slide 24
EN3
24
Ring 3
Ring 2

## Slide 25
RE-2
19.0
19.1
18.1
17.3
19.8
22.7
16.9
19.1
20.4
17
19.4
19.5
19.9
18.2
19.0
19.5
19.5
18.9
18.8
20.5
18.6
21
19.8
19.1
19.2
19.4
18.1
18.8
18.8
18.9
19.4
20
19.1
19.7
20.3
17
17.4
18.4
17.6
19.1
17.2
14.9
20.4
17.3
19.5
19.6
20.5
19.9
20.7
20.3
18.7
17.8
20.6
18.9
19.2
17.5
18.2
18.2
18.7
15.5
18
19.4
19.3
20.3
17.6
17.8
16.6
19.1
19.3
15.1
11.4
17.3
 | Average | 
Ring 2 | 19.10 | 18.70
Ring 3 | 18.40 | 
Odd |  | 18.70
Pair |  | 18.70
UP |  | 18.3
Down |  | 17.2

## Slide 26: 10 days distributions (2-12 August)

## Slide 27
RE-4
17.6
19.0
14.4
19
18.1
17.8
19.6
18.5
19.1
15.9
19
19
19
4.8
18.8
18.8
18.3
17.7
18.9
19.8
18.
18.0
18.3
18.5
18.4
18.5
18.3
1848
17.8
18.1
17.6
18.9
19
 | Average | 
Ring 2 | 17.80 | 17.80
Ring 3 | 17.80 | 
Odd |  | 17.50
Even |  | 18.20
UP |  | 18.3
Down |  | 17.2
18.8
18.9
17.7
17.0
15.7
17.8
18.6
16.4
17
17.7
18.5
17.2
18.8
18.6
18.4
18
18.6
19.4
20.7
18.3
18.1
18.8
14.3
18.4
16.9
16.9
19.2
18.4
17.1
16.4
18.3
17
18.1
14.8
17.1
20.1
15.6
15.1
16.7
August 1st

## Slide 28
RE-3
18.5
23.6
20.2
18.6
20.1
21.7
20.5
20.4
20.2
20.0
20.6
19.2
20.0
19.4
20,2
20
19.5
18.9
19.1
19.2
19.5
19.1
19.6
19.3
20
20
20
20.1
19.8
19
20.1
19.2
20.0
19.9
20.0
19.6
19.1
18.5
19.8
19.7
19.8
19.9
20.0
23.6
19.3
19.1
19.9
20.1
19.3
16.8
21.2
19.5
19.1
19.3
18.8
18.9
19.5
17.8
18.3
22.4
20
19.9
19.1
19.8
19.2
19.7
19.4
19.3
18.8
18.8
19.9
19.4
 | Average | 
Ring 2 | 19.60 | 19.70
Ring 3 | 19.80 | 
Odd |  | 19.70
Even |  | 19.70
UP |  | 19.9
Down |  | 19.4

## Slide 29: Summary table and conclusion (2)
Average temperature 19-200
The RE4 circuit is more effective then RE3-2-1: lower temperature and more stable).
Negative side temperature lowest due to the shaft
 | RE4 | RE3 | RE2 | RE-2 | RE-3 | RE-4
Ring 2 | 18.50 | 19.80 | 19.30 | 19.10 | 19.60 | 17.80
Ring 3 | 18.40 | 19.60 | 19.60 | 18.40 | 19.80 | 17.80
Average | 18.50 | 19.70 | 19.50 | 18.70 | 19.70 | 17.80

## Slide 30: Summary table and conclusion (2)
Average temperature 19-200
The RE4 circuit is more effective then RE3-2-1: lower temperature and more stable).
Negative side temperature lowest due to the shaft
 | RE4 | RE3 | RE2 | RE-2 | RE-3 | RE-4
Ring 2 | 18.50 | 19.80 | 19.30 | 19.10 | 19.60 | 17.80
Ring 3 | 18.40 | 19.60 | 19.60 | 18.40 | 19.80 | 17.80
Average | 18.50 | 19.70 | 19.50 | 18.70 | 19.70 | 17.80

## Slide 31: Comparison between FOS and PT100 (outside and inside chamber)
 |  | RE4 | RE3 | RE2 | RE1 | RE-1 | RE-2 | RE-3 | RE-4
Ring 2 | FOS | 18.50 | 19.40 | 19.50 |  |  | 19.10 | 19.80 | 17.80
 | PT100 |  | 21.20 | 20.20 | 21.40 | 21.00 |  | 22.00 | 
Ring 3 | FOS | 18.00 | 19.70 | 19.80 |  |  | 18.50 | 19.90 | 17.80
 | PT100 |  | 20.50 | 20.10 | 20.30 | 20.20 |  | 21.30 | 
Average | FOS | 18.20 | 19.50 | 19.60 |  |  | 18.70 | 19.80 | 17.80
 | PT100 |  | 20.90 | 20.10 | 20.80 | 20.60 | 21.00 | 21.70 | 
Approximately 1 degrees difference between outside and inside chamber (FOS-PT100).
FOS are not installed in RE1. PT100 are not installed in RE4