## Summary
Total Heat removed for new or modified components |  | LS2 | LS3 | Total L2+LS3
YE+1 and YE-1 | kW | 14.4 | 36 | 50.4
YE+2 and YE-2 | kW | 9.36 | 0 | 9.36
YE+3 & YE-3 | kW | 4.92 | 1.656 | 6.576
|  | 28.68 | 37.656
Flow-Heat Summary for full circuit |  | ENDCAP circuit for 6 disks
| Units | Measures '17-18 | LS2 | LS3
Total flow | m3/h | 76 | 76 | 76
Total Heat | kW | 137.1 | 165.78 | 203.436
Total temperature rise | C | 1.2 | 1.9 | 2.3

## Upgrade YE1
YE1 UPGRADE cooling parameters
ENDCAP COOLING CIRCUIT
|  | LS2 | LS3 | LS3
| Units | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0
Tube/pipe OD | mm | 8 | 8 | 10
Tube/pipe wall | mm | 1 | 1 | 1
Tube/pipe ID | mm | 6 | 6 | 8
Tube/pipe Area | mm2 | 28.26 | 28.26 | 50.24
Flow rate | liter/min | 2 | 2 | 4
Flow velocity | m/sec | 1.1795 | 1.1795 | 1.327
Reynolds | unitless | 6837.8172 | 6837.8172 | 10256.7258
Heat removal/chamber-superchamber | W | 200 | 400 | 600
# chambers/circuit |  | 2 | 1 | 1
Heat removal/circuit | W | 400 | 400 | 600
Temperature rise | C | 2.8708 | 2.8708 | 2.1531
Number of circuits | ea | 18 | 18 | 18
Total flow | lt/min | 36 | 36 | 72
Heat removed | W | 7200 | 7200 | 10800
Heat removal capacity | W
Pressure drop (measured) | bar |  | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1 |  | LS2 | LS3 | Total
Total flow-disk manifold | liter/min
Total Heat removed | kW | 7.2 | 18 | 3.3
Total temperature rise | C
Note on C13: paola tropea: 2 superchambers/circuit (4 chambers in total in series)
Note on D13: paola tropea: 1 superchamber/circuit
Note on E13: paola tropea: 6 chambers @ 100 W each in parallel

## Upgrade YE2
YE2 UPGRADE cooling parameters |  | LS2
ENDCAP COOLING CIRCUIT
| Units | CSC cooling circuit ME2/1, ME3/1
Tube/pipe OD | mm | 9.525
Tube/pipe wall | mm | 0.8128
Tube/pipe ID | mm | 7.8994
Tube/pipe Area | mm2 | 48.9844
Flow rate | liter/min | 4
Flow velocity | m/sec | 1.361
Reynolds | unitless | 10387.3467
Heat removal/chamber | W
# chambers/circuit | #
Additional Heat removal/circuit | W | 390
Temperature rise | C | 1.3995
Number of circuits | ea | 12
Total flow | liter/min | 48
Heat removed | W | 4680
Heat removal capacity | W
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+2 & YE-2 |  | LS2 | LS3 | Total
Total flow | liter/min
Total Heat removed | W | 4.68 | 0 | 4.68
Total temperature rise | C
ME2/1, ME3/1 heat per circuit rises to 780 W instead of 390 W (doubles due to new electronic)
Additional heat per circuit is 390 W

## Upgrade YE3
YE3 UPGRADE cooling parameters |  | Replacement of electronics LS2
|  |  | New chambers LS3 | New chambers LS3
| Units | CSC cooling circuit ME4/1 | RPC cooling circuit RE3/1 | RPC cooling circuit RE4/1
Tube/pipe OD | mm | 9.525 | 8 | 8
Tube/pipe wall | mm | 0.8128 | 1 | 1
Tube/pipe ID | mm | 7.8994 | 6 | 6
Tube/pipe Area | mm2 | 48.9844 | 28 | 28
Flow rate | liter/min | 4 | 2 | 2
Flow velocity | m/sec | 1.361 | 1.2 | 1.2
Reynolds | unitless | 10387.3467 | 6838 | 6838
Heat removal/chamber | W
# chambers/circuit | #
Heat removal/circuit | W | 410 | 23 | 23
Temperature rise | C | 1.4713 | 0.2 | 0.2
Number of circuits | ea | 6 | 18 | 18
Total flow | liter/min | 24 | N/A | N/A
Heat removed | W | 2460 | 414 | 414
Heat removal capacity | W
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3 |  | LS2 | LS3 | Total
Total flow | liter/min
Total Heat removed | kW | 2.46 | 0.828 | 3.288
Total temperature rise | C
ME4/1heat per circuit rises to 780 W instead of 370 W