## Sheet1
|  |  | Cable Volt drop and Power Lose | [7 empty] | Voltage = | 5 | [Volts]
[8 empty] | Ian 5 July 2018 |  |  | Current = | 3 | [Amps]
[6 empty] | Two cables per chamber |  |  |  |  | Power lose = I^2 X R |  | [Watts}
Attention the voltage drop and power lose are in both conducters
|  | Cable type | Cable section | Cable Length | Resistance per length | Temperature of cable | Resistance for cable length | Voltage drop | Power Lose | Power lose | Power lose | Power per FEB | Power FEB per Station | Percent power lose Cable wrt FEB
[9 empty] | cable | Station | CMS
|  |  | [mm2] | [m] | [Ohm/km] | [deg. Celsuis] | [Ohm] | [V] | [W] | [W] | [W] | [W] | [W] | [%]
Power | SCEM | 04.08.82.040.2 | 4 | 15 | 5.7 | 20 ? | 0.0855 | 0.513 | 1.539 | 55.404 | 221.616 | 15 | 540 | 10.26
Sense | SCEM | 04.21.51.102.4 | 0.5 | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 15 | 540 | 0
|  |  | 1.5 | 15 | 11.4 | 25 | 0.171 | 1.026 | 3.078 | 110.808 | 443.232 | 15 | 540 | 20.52
| ProfiBus | 04.21.60.300.9 | 0.88 | 15 | 20 | 25 ? | 0.3 | 1.8 | 5.4 | 194.4 | 777.6 | 15 | 540 | 36
|  | RPC LB LV | 2.5 | 30 | 7 | 25 | 0.21 | 1.26 | 3.78 | 136.08 | 544.32 | 15 | 540 | 25.2
REF;
http://www.epanorama.net/index/calc_cable_index.html
https://www.electricalengineeringtoolbox.com/2016/01/resistance-and-reactance-per-km-of.html
https://www.owenduffy.net/calc/WireDcResistance.htm
| Good | http://mustcalculate.com/electronics/wireproperties.php?mat=cu&l=15&area=4&areae=mm2&i=3&temp=25