### Standardised records of subdetector sessions

to develop needed alarms-3

ECAL

| # Risks | # Location and Type of Protection | # DCS* action | # al2 | # al3 | # Level-3 action | # Remaining # questions |
| --- | --- | --- | --- | --- | --- | --- |
| - from IS-37: |  |  |  |  |  |  |
| - fire | distributed smoke sniffers: - lowest VESDA level - interm.VESDA or several - high VESDA or repeat | observation and soft shutdow | x | x | prev.inertion powercut,inert | location switching sequence |
| - gases | none |  |  |  |  |  |
| - oxygen | air/N2 sweeping |  |  |  |  | location, capac. |
| - water | up to 100 ltr/sec, flow sensors | shut-down | x |  | prev.inertion | which neighbours affected, other coolants, type of sensor, thresholds,slow shut-down |
| - humidity | Air/N2 sweeping, front-end “capteurs” to DCS | leak-estimate |  |  |  | location, thresholds |
| - add-ons: |  |  |  |  |  |  |
| - volts to 400V | front-end amps to DCS | interlocks+ cuts |  |  |  | breakers, intervention-levels |
| - po. to 160kw |  |  |  |  |  | kw/m3, fuses,breakers |
| - temperature | calibration, some to DCS | display |  |  |  | what selection,inertion |
| - cryo-leaks |  |  |  |  |  |  |
| - others |  |  |  |  |  |  |

* this is the Detector Control System or any other “slow control system”; how many of those we will eventually have in LHC has to be 	followed with great caution

HCAL

| # Risks | # Location and Type of Protection | # DCS* action | # al2 | # al3 | # Level-3 action | # Remaining # questions |
| --- | --- | --- | --- | --- | --- | --- |
| - from IS-37: |  |  |  |  |  |  |
| - fire | smoke sniffers in ends: - lowest VESDA level - interm.+high VESDA | observation display | x |  | prev.inertion | location , layout accord. surface experience switching sequence |
| - gases | none |  |  |  |  |  |
| - oxygen | air/N2 sweeping |  |  |  |  | location, capac. |
| - water | return-flow sensors | display, shut-down | x |  | prev.inertion | max.flow,which neighbours affected, other coolants, type of sensor, slow shutdown |
| - humidity | Air/N2 sweeping, read-out box dry N2 purge | leak-estimate |  |  |  | location, threshold, which N2 system |
| - add-ons: |  |  |  |  |  |  |
| - volts to 12k | photodetectors to DCS |  |  |  |  | actions, parts |
| - amps | high-current,low-volt electronic |  |  |  |  | actions, parts |
| - power |  |  |  |  |  | kw, fuses, breakers |
| - temperature | - selection to DCS - read-out box | display, slow shutd. | x |  | prev.inertion |  |
| - cryo-leaks |  |  |  |  |  |  |
| - others |  |  |  |  |  | All of HF + 53 degree crack still to be analysed |

HCAL side-issues (see also consolidated risk-list)

- Fulguera shops safety

- Bldg. 186 safety/refurbishing

- Surface assy,tests and records

- Trialfit down the pit, hoists and friction pads

- Subterranean assy and maintenance

* this is a “slow control system” of any kind; how many of those we will eventually have in LHC has to be 	followed with great caution

MAGNET

| # Risks | # Location and Type of Protection | # DCS* action | # al2 | # al3 | # Level-3 action | # Remaining # questions |
| --- | --- | --- | --- | --- | --- | --- |
| - from IS-37: |  |  |  |  |  |  |
| - fire | no smoke detection inside |  |  |  |  | confirmation |
| - gases | none flammable |  |  |  |  |  |
| - oxygen | in cavern - for small He leak - for large He leak | ramp-down |  | x |  | threshold delayed additional action |
| - water | several ltr/sec to vac.pump | ramp-down |  |  |  | which neighbours affected, type of sensor, threshold |
| - humidity |  | leak-estimate |  |  |  | would enter which medium |
| - add-ons: |  |  |  |  |  |  |
| - volts | deterioration of insulation | ramp-down |  |  |  | breakers, fuses, volts or amps, intervention-levels |
| - power |  |  |  |  |  | dito |
| - temperature | deviation from calibration | display |  |  |  | thresholds |
| - cryo-leaks | ( see oxygen) |  |  |  |  |  |
| - vacuum | loss | ramp-down |  |  |  | what type of sensor, thresholds |
| - mechanics | Strain-gages on tie-rods | ramp-down | x |  |  | thresholds, slow shut-down of neighbours |
| - others |  |  |  |  |  |  |

* this is a “slow control system” of any kind; how many of those we will eventually have in LHC has to be 	followed with great caution

MUON

| # Risks | # Location and Type of Protection | # DCS* action | # al2 | # al3 | # Level-3 action | # Remaining # questions |
| --- | --- | --- | --- | --- | --- | --- |
| - from IS-37: |  |  |  |  |  |  |
| - fire | 1. alignement system, 36 pieces: no major risks apparent for unattended operation 2. barrel drift chambers gas: Argon/C02 - inlet and outlet temperatures, all in front end - smoke detection 3. RPC's: barrel types produce 20 kw, endcaps more; bakelite is construction material and possible fire hazard, the chambers are slightly temperature sensitive (minus 10 degrees) and are monitored via half-open surfaces 4. CSCs,gas: Ar/C02/CF4 front end with pre-amplifier and drivers are water cooled, in their copper box | surveillance via some temperature sensors observation and soft shutdow operational temperature monitoring if water temperature deviates | X X x | x | prev.inertion fast power shut-down, gas shut-off, inertion | location, thresholds sniffers and/or infrared smoke detection to be checked for its efficacy, environmental compatibility, possibly placing sending and receiving ends on outside, with mirrors on the inside; tightening outside surface for inertion thresholds, location, effectiveness which action |
| - gases | barrel drift chambers gas: Argon/C02 RPC gas mixing errors is monitored and corrected from the surface | monitoring, automatic gas shutoff | X x |  |  | where, thresholds definition of actions |
| - oxygen | during temporary N2 inertion | monitoring |  |  |  | location, thresholds, actions |
| - water | barrel drift chambers: large coolant leaks via flow-imbalance; small leak below | slow shut-down, gas shut off, | x |  | prev.inertion | which neighbours affected, thresholds, slow shut-down |
| - humidity | barrel drift chambers: front-end sensors | warning, leak-estimate |  |  |  | location, thresholds |
| - add-ons: |  |  |  |  |  |  |
| - volts | RPC high and low voltage | interlocks+ power cuts |  |  |  | breakers, intervention-levels |
| - power | see: fire |  |  |  |  | kw/m3, fuses, breakers |
| - temperature | barrel drift chambers inlet and outlet temperatures, | monitor/display from front end |  |  |  | what selection, inertion |
| - cryo-leaks | not applicable |  |  |  |  |  |
| - others |  |  |  |  |  |  |

* this is the Detector Control System or any other “slow control system”; how many of those we will eventually have in LHC has to be 	followed with great caution

TRACKER

| # Risks | # Location and Type of Protection | # DCS* action | # al2 | # al3 | # Level-3 action | # Remaining # questions |
| --- | --- | --- | --- | --- | --- | --- |
| - from IS-37: |  |  |  |  |  |  |
| - fire | 1.detector areas, permanently inerted by dry, cold N2 2.front-ends and patch-panels: distributed smoke sniffers: - lowest VESDA level - interm.VESDA or several - high VESDA or repeat | see gases, temperatures observation and soft shutdow | x | x | prev.inertion powercut,inert | location switching sequence |
| - gases | DME in Neon, leaks monitored in Neon, N2 and via detector physics performance | soft shut-down of gas and power-supplies | x |  |  | thresholds to be developed, gas-supply reliability |
| - oxygen | N2 sweeping to be monitored for DME and oxygen high oxygen, could lead to hazard together with DME and/or hot components | prealarm at low oxygen level, actions as above | x | x |  | locations, capacity, thresholds thresholds |
| - water | Fluor-carbon is coolant throughout, waterleaks from ECAL (up to 100 ltr/sec) and other subdetectors could pose problem | see humidity |  |  |  |  |
| - humidity | in N2 circuit, front-end “capteurs” to DCS - low level - high level | warning, leak-estimate, soft shut-down | x | x | powercut | location, thresholds and type of sensors, which neighbours, scenarios, slow shut-down plan |
| - add-ons: |  |  |  |  |  |  |
| - volts to 600V | front-end amps to DCS | interlocks+ cuts |  |  |  | breakers, intervention-levels |
| - po. to 50kw |  |  |  |  |  | kw/m3, fuses,breakers |
| - temperature | -for operational control to DCS -larger deviation in combination with oxygen | display soft shut-down | x |  |  | threshold, selection, N2 flow-increase |
| - operator error |  |  |  |  |  | scenarios, interlocks and consequences to be defined |
| - others |  |  |  |  |  |  |

* this is the Detector Control System or any other “slow control system”; how many of those we will eventually have in LHC has to be 	followed with great caution