## Sheet1
Leak rates of Cu cooling assemblies : RE4/3, Cu pipe length = 400 cm, volume = 0.113 litres
[11 empty] | F/0.6 | Gx 1.13
PILOT PRODUCTION FOR RE4 : October 2012
SN | Filename | Valve A | Specifications | Fabricated at | dp/dt | dp/dt | leak rate | Remarks | Packed | Filename
[5 empty] | (10-4) bar/min | (10-3) mbar/s | (10-4) mbar.litre/s
1 | RE4/3-001-06092012.plw | closed | Brass ferrules | MDPDD | -2.845 | #VALUE! | -5.358 | OK | YES-CERN | RE4/3-001-06092012.plw
2 | RE4/3-001-12102012.plw | open | Brass ferrules | MDPDD | -7.434 | -12.39 | -14.001 |  |  | RE4/3-001-12102012.plw
3 | RE4/3-002-12102012.plw | closed | SS ferrules, ferrule cripmed at improper place | GEW | -43.9 | -73.167 | -82.679 |  | REJECT | RE4/3-002-12102012.plw
4 | RE4/3-003-16102012.plw | closed | SS ferrules, not crimped properly | MDPDD | -83 | -138.333 | -156.316 |  |  | RE4/3-003-16102012.plw
5 | RE4/3-003-17102012-1120h.plw | closed | SS ferrules, crimped properly | MDPDD | -31.6 | -52.667 | -59.514 |  |  | RE4/3-003-17102012-1120h.plw
6 | RE4/3-004-17102012-1455h.plw | closed | Brass ferrules, crimped properly | MDPDD | -13.9 | -23.167 | -26.179 |  |  | RE4/3-004-17102012-1455h.plw
7 | RE4/3-004-17102012-1740h.plw | closed | Brass ferrules, crimped properly, tightened further | MDPDD | -10.9 | -18.167 | -20.529 | OK | YES-GENT | RE4/3-004-17102012-1740h.plw
8 | RE4/3-005-18102012-1045h.plw | closed | SS ferrules, crimped properly, extended length | GEW | -9.815 | -16.366 | -18.5 |  |  | RE4/3-005-18102012-1045h.plw
9 | RE4/3-005-18102012-1335h.plw | closed | Brass ferrules, crimped properly, extended length | GEW | -6.7 | -11.16 | -12.61 |  |  | RE4/3-005-18102012-1335h.plw
10 | RE4/3-005-18102012-1615h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -0.177 | -0.295 | -0.333 | OK | YES-CERN | RE4/3-005-18102012-1615h.plw
11 | RE4/3-006-19102012-1100h.plw | closed | SS ferrules, crimped properly, In required length, Threading damaged | GEW | -13.7 | -22.83 | -25.79 |  | REJECT | RE4/3-006-19102012-1100h.plw
12 | RE4/3-007-19102012-1435h.plw | closed | SS ferrules, crimped properly, In required length, | GEW | -1.475 | -2.458 | -2.775 | OK | YES-CERN | RE4/3-007-19102012-1435h.plw
13 | RE4/3-008-20102012-0950h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -2.19 | -3.65 | -4.125 | OK | YES-CERN | RE4/3-008-20102012-0950h.plw
14 | RE4/3-009-20102012-1450h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -7.01 | -11.68 | -13.2 |  | YES-GENT | RE4/3-009-20102012-1450h.plw
15 | RE4/3-009-20102012-1630h.plw | closed | SS ferrules, crimped properly, In required length, long term | GEW | [5 empty] | RE4/3-009-20102012-1630h.plw
16 | RE4/3-009-21102012-0915h.plw | closed | SS ferrules, crimped properly, In required length, run aborted after 2 min | GEW | [5 empty] | RE4/3-009-21102012-0915h.plw
17 | RE4/3-010-21102012-1000h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -0.456 | -0.76 | -0.8588 | OK | YES-CERN | RE4/3-010-21102012-1000h.plw
18 | RE4/3-011-21102012-1330h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -8.43 | -14.05 | -15.87 | OK | YES-GENT | RE4/3-011-21102012-1330h.plw
19 | RE4/3-012-22102012-1000h.plw | closed | SS ferrules, crimped properly, In required length | GEW | -5.96 | -9.93 | -11.24 | OK | YES-GENT | RE4/3-012-22102012-1000h.plw
20 | RE4/3-013-22102012-1355h.plw | closed | SS ferrules, crimped properly, In required length, double slots in plates | GEW | -4.84 | -8.06 | -9.11 | OK | YES-GENT | RE4/3-013-22102012-1355h.plw
21 | RE4/2-001-23102012-1410h.plw | closed | SS ferrules, crimped properly | MDPDD | -4.3 | -7.16 | -8.09 | OK | YES-CERN | RE4/2-001-23102012-1410h.plw
22 | RE4/2-002-24102012-1115h.plw | closed | SS ferrules, crimped properly | MDPDD | -2.754 | -4.59 | -5.1867 | OK | YES-CERN | RE4/2-002-24102012-1115h.plw
23 | RE4/2-003-24102012-1330h.plw | closed | SS ferrules, crimped properly | MDPDD | -0.336 | -0.56 | -0.632 | OK | YES-CERN | RE4/2-003-24102012-1330h.plw
24 | RE4/2-004-25102012-0830h.plw | closed | SS ferrules, crimped properly | MDPDD | -2.12 | -3.53 | -3.99 | OK | YES-CERN | RE4/2-004-25102012-0830h.plw
25 | RE4/2-005-25102012-1200h.plw | closed | SS ferrules, crimped properly | MDPDD | -2.095 | -3.49 | -3.94 | OK | YES-CERN | RE4/2-005-25102012-1200h.plw
26 | RE4/3-014-26102012-1115h.plw | closed | SS ferrules, crimped properly, In required length | MDPDD | -31.1 |  |  |  |  | RE4/3-014-26102012-1115h.plw
27 | RE4/3-015-26102012-1450h.plw | closed | SS ferrules, crimped properly, In required length | MDPDD | -0.649 | -1.08 | -1.22 | OK | YES-GENT | RE4/3-015-26102012-1450h.plw
28 | RE4/3-003-27102012-1235h.plw | closed | SS ferrules, crimped properly, In required length | MDPDD | -5.409 | -9.015 | -10.186 | OK | YES-GENT | RE4/3-003-27102012-1235h.plw
29 | RE4/3-016-27102012-1515h.plw | closed | SS ferrules, crimped properly, In required length, fit (30-60) min | MDPDD | -10.8 | -18 | -20.34 | OK | YES-GENT | RE4/3-016-27102012-1515h.plw
30 | RE4/3-016-27102012-1515h.plw | closed | SS ferrules, crimped properly, In required length, straight end (120-240m) | MDPDD | -0.0243 |  |  |  |  | RE4/3-016-27102012-1515h.plw
31 | RE4/3-016-27102012-1515h.plw | closed | SS ferrules, crimped properly, In required length, straight end (400-1200 m) | MDPDD | -3.155 |  |  |  |  | RE4/3-016-27102012-1515h.plw
30 | RE4/3-016-29102012-0810h.plw | closed | SS ferrules, crimped properly, In required length, straight end | MDPDD | -11.4 | -19 | -21.47 |  |  | RE4/3-016-29102012-0810h.plw
31 | RE4/3-014-29102012-1015h.plw | closed | SS ferrules, crimped properly, In required length | MDPDD | -12.3 | -20.5 | -23.165 | OK | YES-GENT | RE4/3-014-29102012-1015h.plw
32 | RE4/3-017-29102012-1300h.plw | closed | SS ferrules, crimped properly, In required length, | MDPDD | -4.3 | -7.16 | -8.1 | OK | YES-GENT | RE4/3-017-29102012-1300h.plw
33
CONTINUED MEASUREMENTS FOR RE4 : January 2013
leak rate
(10-4) mbar.litre/s
34 | RE42-006-25012013-1438h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 3.12 | OK | YES-BARC | RE42-006-25012013-1438h.plw | CMS-RE4-2-BARC-005
35 | RE42-007-30012013-1700h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 1.48, 2.70 | OK | YES-BARC | RE42-007-30012013-1700h.plw | CMS-RE4-2-BARC-007
36 | RE42-008-31012013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 2.06, 4.49. 0.06 | OK | YES-CERN/GENT | RE42-008-31012013-1410h.plw |  |  | 2013-03-13
37 | RE42-009-01022013-1320h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 2.2, 0.55, 1.76 | OK | YES-CERN/GENT | RE42-009-01022013-1320h.plw |  |  | 2013-03-13
38 | RE42-010-05022013-1050h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 1.21, 2.32, 1.02 | OK | YES-CERN/GENT | RE42-010-05022013-1050h.plw |  |  | 2013-03-13
39 | RE43-018-05022013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 1.82, 1.49, 1.21 | OK | YES-CERN/GENT | RE43-018-05022013-1430h.plw
40 | RE43-019-06022013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.99, 0.95, 1.04 | OK | YES-CERN/GENT | RE43-019-06022013-1200h.plw
41 | RE43-020-06022013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.59, 0.49, 0.49 | OK | YES-CERN/GENT | RE43-020-06022013-1440h.plw
42 | RE43-021-07022013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.42, 0.5 | OK | YES-CERN/GENT | RE43-021-07022013-0950h.plw
43 | RE43-021-07022013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.59 | OK | YES-CERN/GENT | RE43-021-07022013-1200h.plw
44 | RE43-022-07022013-1350h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.13, 0.25, 0.13 | OK | YES-CERN/GENT | RE43-022-07022013-1350h.plw
45 | RE42-011-25022013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.50, 1.35, 0.90 | OK | YES-CERN/GENT | RE42-011-25022013-1130h.plw |  |  | 2013-03-13
46 | RE42-012-25022013-1600h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.10, 0.19, 0.17 << 5 | OK | YES-CERN/GENT | RE42-012-25022013-1600h.plw |  |  | 2013-03-13
47 | RE42-013-06032013-1800h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.70, 0.45, 0.06 << 5 | OK | YES-BARC | RE42-013-06032013-1800h.plw | CMS-RE4-2-BARC-009
48 | RE43-023-12032013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.48, 0.65, 0.41 << 5 | OK | YES-CERN/GENT | RE43-023-12032013-1430h.plw |  |  | May-13-1
49 | RE42-014-13032013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.29, 0.20, 0.22 << 5 | OK |  | RE42-014-13032013-1100h.plw | Not Acceptable because of incorrect design
50 | RE42-015-25032013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.00, 1.29, 1.78 << 5 | OK | YES-BARC | RE42-015-25032013-1030h.plw | CMS-RE4-2-BARC-019
51 | RE43-024-02042013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.17, 0.39, 0.29 << 5 | OK | YES-CERN/GENT | RE43-024-02042013-1100h.plw |  |  | 2013-04-01
52 | RE43-025-02042013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.48, 0.09 << 5 | OK | YES-CERN/GENT | RE43-025-02042013-1430h.plw |  |  | 2013-04-01
53 | RE43-025-03042013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.23 << 5 | OK | YES-CERN/GENT | RE43-025-03042013-1000h.plw
54 | RE43-026-03042013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 2.57, 0.31, 0.33 << 5 | OK | YES-CERN/GENT | RE43-026-03042013-1200h.plw |  |  | 2013-04-01
55 | RE43-027-03042013-1530h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.27, 0.52, 1.78 << 5 | OK | YES-CERN/GENT | RE43-027-03042013-1530h.plw |  |  | 2013-04-01
56 | RE43-028-03042013-1730h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.23, 1.96, 0.23 << 5 | OK | YES-CERN/GENT | RE43-028-03042013-1730h.plw |  |  | 2013-04-01
57 | RE43-029-04042013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.65, 1.22, 0.55 << 5 | OK | YES-CERN/GENT | RE43-029-04042013-1200h.plw |  |  | 2013-04-01
58 | RE43-030-04042013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.30, 0.25, 0.18 << 5 | OK | YES-CERN/GENT | RE43-030-04042013-1430h.plw |  |  | 2013-04-01
59 | RE43-031-05042013-1045h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.21, 0.25, 0.25 << 5 | OK | YES-CERN/GENT | RE43-031-05042013-1045h.plw |  |  | 2013-04-01
60 | RE43-032-05042013-1345h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.25, 1.91, 0.60 << 5 | OK | YES-CERN/GENT | RE43-032-05042013-1345h.plw |  |  | 2013-04-01
61 | RE43-033-05042013-1630h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.03 << 5 | OK | YES-CERN/GENT | RE43-033-05042013-1630h.plw |  |  | 2013-04-01
62 | RE43-033-08042013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.08, 0.46 << 5 | OK | YES-CERN/GENT | RE43-033-08042013-1000h.plw
63 | RE42-016-08042013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.24, 0.15, 0.22 << 5 | OK | YES-BARC | RE42-016-08042013-1130h.plw | CMS-RE4-2-BARC-021
64 | RE42-017-08042013-1500h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.42, 0.25, 0.25 << 5 | OK | YES-CERN | RE42-017-08042013-1500h.plw |  |  | 2013-04-01
65 | RE42-018-09042013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.17, 0.25 << 5 | OK | YES-CERN | RE42-018-09042013-1020h.plw |  |  | 2013-04-01
66 | RE42-019-09042013-1300h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.09, 0.08, 0.03 << 5 | OK | YES-CERN | RE42-019-09042013-1300h.plw |  |  | 2013-04-01
67 | RE42-020-09042013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.72, 0.84, 0.61 << 5 | OK | YES-CERN | RE42-020-09042013-1430h.plw |  |  | 2013-04-01
68 | RE42-021-10042013-1515h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | << 5 | NOK | ??? | RE42-021-10042013-1515h.plw | UNDER INVESTIGATION
69 | RE42-022-10042013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.55, 0.22 << 5 | OK | YES-CERN | RE42-022-10042013-1000h.plw |  |  | 2013-04-01
70 | RE42-023-10042013-11100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.22, 0.22 << 5 | OK | YES-CERN | RE42-023-10042013-11100h.plw |  |  | 2013-04-01
71 | RE42-024-10042013-1315h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.88, 0.55 << 5 | OK | YES-CERN | RE42-024-10042013-1315h.plw |  |  | 2013-04-01
72 | RE42-025-15042013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.77 << 5 | OK | YES-CERN | RE42-025-15042013-1100h.plw |  |  | 2013-04-01
73 | RE42-026-15042013-1415h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.43, 1.43, 0.91 << 5 | OK | YES-CERN | RE42-026-15042013-1415h.plw |  |  | 2013-04-01
74 | RE42-027-15042013-1730h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 7.81. 12.1 >> 5 | Not OK |  | RE42-027-15042013-1730h.plw | UNDER INVESTIGATION
75 | RE42-027-16042013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.55, 0.44, 0.33 << 5 | OK | YES-CERN | RE42-027-16042013-1000h.plw |  |  | 2013-04-01
76 | RE42-028-18042013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.32, 1.87, 1.98 << 5 | OK | YES-BARC | RE42-028-18042013-1430h.plw | CMS-RE4-2-BARC-022
77 | RE42-029-25042013-1645h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.55, 0.22 << 5 | OK | YES-BARC |  | CMS-RE4-2-BARC-023
78 | RE42-029-26042013-1310h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.33 << 5 | OK | YES-BARC |  | CMS-RE4-2-BARC-023
79 | RE42-030-26042013-1445h.plw | closed | Brass ferrules, crimped properly, In required length, | MDPDD |  |  | 0.55, 0.44, 0.33 << 5 | OK | YES-BARC |  | CMS-RE4-2-BARC-024
80 | RE42-031-27042013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.66 << 5 | OK | YES-CERN | RE42-031-27042013-1400h.plw |  |  | May-13-1
81 | RE42-031-28042013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.31 << 5 | OK | YES-CERN | RE42-031-28042013-1200h.plw
82 | RE42-032-28042013-1245h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.44 << 5 | OK | YES-CERN | RE42-032-28042013-1245h.plw |  |  | May-13-1
83 | RE42-032-29042013-0815h.plw |  |  | Hi-Tech |  |  | 1.10 << 5 | OK | YES-CERN | RE42-032-29042013-0815h.plw
84 | RE42-033-29042013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.44 << 5 | OK | YES-CERN | RE42-033-29042013-1130h.plw |  |  | May-13-1
85 | RE42-034-29042013-1345h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.33 << 5 | OK | YES-CERN | RE42-034-29042013-1345h.plw |  |  | May-13-1
86 | RE42-035-29042013-1500h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.11 << 5 | OK | YES-CERN | RE42-035-29042013-1500h.plw |  |  | May-13-1
87 | RE42-036-29042013-1700h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.03, 0.03 << 5 | OK | YES-CERN | RE42-036-29042013-1700h.plw |  |  | May-13-1
88 | RE42-037-30042013-0945h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.33 << 5 | OK | YES-CERN | RE42-037-30042013-0945h.plw |  |  | May-13-1
89 | RE42-038-30042013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.22 << 5 | OK | YES-CERN | RE42-038-30042013-1200h.plw |  |  | May-13-1
90 | RE42-039-30042013-1315h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.55, 0.33 << 5 | OK | YES-CERN | RE42-039-30042013-1315h.plw |  |  | May-13-1
91 | RE42-040-30042013-1450h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.44, 0.22 << 5 | OK | YES-CERN | RE42-040-30042013-1450h.plw |  |  | May-13-1
92 | RE43-034-30042013-1640h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.91, 0.26 << 5 | OK | YES-CERN/GENT | RE43-034-30042013-1640h.plw |  |  | May-13-1
93 | RE43-035-01052013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.03, 0.01 << 5 | OK | YES-CERN/GENT | RE43-035-01052013-0940h.plw |  |  | May-13-1
94 | RE43-036-01052013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.13 << 5 | OK | YES-CERN/GENT | RE43-036-01052013-1200h.plw |  |  | May-13-1
95 | RE43-037-01052013-1600h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.26 << 5 | OK | YES-CERN/GENT | RE43-037-01052013-1600h.plw |  |  | May-13-1
96 | RE43-038-01052013-1750h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.05, 0.01 << 5 | OK | YES-CERN/GENT | RE43-038-01052013-1750h.plw |  |  | May-13-1
97 | RE43-039-02052013-1050h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.08 << 5 | OK | YES-CERN/GENT | RE43-039-02052013-1050h.plw |  |  | May-13-1
98 | RE43-040-02052013-1230h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.39, 0.39 << 5 | OK | YES-CERN/GENT | RE43-040-02052013-1230h.plw |  |  | May-13-1
99 | RE43-041-02052013-1520h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.65, 0.65 << 5 | OK | YES-CERN/GENT | RE43-041-02052013-1520h.plw |  |  | May-13-1
100 | RE43-042-02052013-1710h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.52, 0.65 << 5 | OK | YES-CERN/GENT | RE43-042-02052013-1710h.plw |  |  | May-13-1
101 | RE43-043-06052013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.65, 0.26 << 5 | OK | YES-CERN/GENT | RE43-043-06052013-0950h.plw |  |  | May-13-2
102 | RE43-044-09052013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26 << 5 | OK | YES-CERN/GENT | RE43-044-09052013-1040h.plw |  |  | May-13-2
103 | RE43-045-09052013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.52, 0.52 << 5 | OK | YES-CERN/GENT | RE43-045-09052013-1200h.plw |  |  | May-13-2
104 | RE43-046-09052013-1540h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.39 << 5 | OK | YES-CERN/GENT | RE43-046-09052013-1540h.plw |  |  | May-13-2
105 | RE43-047-10052013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.13 << 5 | OK | YES-CERN/GENT | RE43-047-10052013-0950h.plw |  |  | May-13-2
106 | RE43-048-10052013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.65, 0.52 << 5 | OK | YES-CERN/GENT | RE43-048-10052013-1410h.plw |  |  | May-13-2
107 | RE43-049-10052013-1610h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.26 << 5 | OK | YES-CERN/GENT | RE43-049-10052013-1610h.plw |  |  | May-13-2
108 | RE43-050-13052013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.26 << 5 | OK | YES-CERN/GENT | RE43-050-13052013-1000h.plw |  |  | May-13-2
109 | RE43-051-13052013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.39, 0.39 << 5 | OK | YES-CERN/GENT | RE43-051-13052013-1410h.plw |  |  | May-13-2
110 | RE43-052-13052013-1700h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.39 << 5 | OK | YES-CERN/GENT | RE43-052-13052013-1700h.plw |  |  | May-13-2
111 | RE43-053-14052013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.65, 0.52 << 5 | OK | YES-GENT | RE43-053-14052013-1130h.plw |  |  | July-13-end
112 | RE42-041-15052013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.55, 0.33, 0.11 << 5 | OK | YES-CERN | RE42-041-15052013-1400h.plw |  |  | May-13-2
113 | RE42-042-16052013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 1.10, 0.33 << 5 | OK | YES-CERN | RE42-042-16052013-1200h.plw |  |  | May-13-2
114 | RE42-043-16052013-1600h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.33, 0.44, 0.22 << 5 | OK | YES-CERN | RE42-043-16052013-1600h.plw |  |  | May-13-2
115 | RE42-044-17052013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.44 << 5 | OK | YES-CERN | RE42-044-17052013-0950h.plw |  |  | May-13-2
116 | RE42-045-17052013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.11 << 5 | OK | YES-CERN | RE42-045-17052013-1200h.plw |  |  | May-13-2
117 | RE42-046-17052013-1510h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.11 << 5 | OK | YES-CERN | RE42-046-17052013-1510h.plw |  |  | May-13-2
118 | RE42-047-20052013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.02, 0.33, 0.33 << 5 | OK | YES-CERN | RE42-047-20052013-1040h.plw |  |  | May-13-2
119 | RE42-048-20052013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.10, 0.22 << 5 | OK | YES-CERN | RE42-048-20052013-1410h.plw |  |  | May-13-2
120 | RE42-049-21052013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.22 << 5 | OK | YES-CERN | RE42-049-21052013-0950h.plw |  |  | May-13-2
121 | RE42-050-21052013-1330h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11, 0.11 << 5 | OK | YES-CERN | RE42-050-21052013-1330h.plw |  |  | May-13-2
122 | RE43-054-23052013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.08, 0.13 << 5 | OK | YES-GENT | RE43-054-23052013-1030h.plw |  |  | July-13-end
123 | RE43-055-03072013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.78 << 5 | OK | YES-GENT | RE43-055-03072013-1440h.plw |  |  | July-13-end
124 | RE43-056-04072013-1140h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.52, 0.52, 0.39 << 5 | OK | YES-GENT | RE43-056-04072013-1140h.plw |  |  | July-13-end
125 | RE43-057-04072013-1540h.plw & RE43-057-05072013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.78, 0.78 << 5 | OK | YES-GENT | RE43-057-04072013-1540h.plw & RE43-057-05072013-1100h.plw |  |  | July-13-end
126 | RE43-058-18072013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.39, 0.26, 0.39 << 5 | OK | YES-GENT | RE43-058-18072013-1030h.plw |  |  | July-13-end
127 | RE43-059-18072013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.65, 1.04, 0.91 << 5 | OK | YES-GENT | RE43-059-18072013-1430h.plw |  |  | July-13-end
128 | RE43-060-19072013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.13, 0.26 << 5 | OK | YES-GENT | RE43-060-19072013-1130h.plw |  |  | July-13-end
129 | RE43-061-19072013-1530h.plw & RE43-061-22072013-1050h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.39 << 5 | OK | YES-GENT | RE43-061-19072013-1530h.plw & RE43-061-22072013-1050h.plw |  |  | July-13-end
130 | RE43-062-22072013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.26 << 5 | OK | YES-GENT | RE43-062-22072013-1130h.plw |  |  | July-13-end
131 | RE43-063-22072013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.91, 0.13, 0.26 << 5 | OK | YES-GENT | RE43-063-22072013-1440h.plw |  |  | July-13-end
132 | RE43-064-22072013-1650h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26 << 5 | OK | YES-GENT | RE43-064-22072013-1650h.plw |  |  | July-13-end
133 | RE43-064-23072013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26 << 5 | OK | YES-GENT | RE43-064-23072013-0950h.plw |  |  | July-13-end
134 | RE43-065-23072013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.78, 0.26, 0.26 << 5 | OK | YES-GENT | RE43-065-23072013-1130h.plw |  |  | July-13-end
135 | RE43-066-23072013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.02, 0.02, 0.13, 0.04 << 5 | OK | YES-CERN/GENT | RE43-066-23072013-1130h.plw |  |  | Aug end 13
136 | RE43-067-24072013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.39, 0.26, 0.26 << 5 | OK | YES-GENT | RE43-067-24072013-1000h.plw |  |  | July-13-end
137 | RE43-068-24072013-1150h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.26 << 5 | OK | YES-GENT | RE43-068-24072013-1150h.plw |  |  | July-13-end
138 | RE43-069-24072013-1500h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.39 << 5 | OK | YES-GENT | RE43-069-24072013-1500h.plw |  |  | July-13-end
139 | RE43-070-25072013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.26, 0.26 << 5 | OK | YES-GENT | RE43-070-25072013-1020h.plw |  |  | July-13-end
140 | RE43-071-25072013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.13, 0.13 << 5 | OK | YES-GENT | RE43-071-25072013-1440h.plw |  |  | July-13-end
141 | RE43-072-25072013-1720h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13 << 5 | OK | YES-GENT | RE43-072-25072013-1720h.plw |  |  | July-13-end
142 | RE43-072-26072013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26 << 5 | OK | YES-GENT | RE43-072-26072013-0940h.plw |  |  | July-13-end
143 | RE43-073-26072013-1200h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.30, 0.52, 0.13 << 5 | OK | YES-GENT | RE43-073-26072013-1200h.plw |  |  | July-13-end
144 | RE43-074-26072013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.26, 0.13 << 5 | OK | YES-CERN/GENT | RE43-074-26072013-1430h.plw |  |  | Aug end 13
145 | RE43-075-29072013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.02, 0.01 ,0.14 << 5 | OK | YES-CERN/GENT | RE43-075-29072013-1100h.plw |  |  | Aug end 13
146 | RE43-076-23082013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.15 ,0.12 << 5 | OK | YES-CERN/GENT | RE43-076-23082013-1020h.plw |  |  | Aug end 13
147 | RE43-077-23082013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.90, 0.40 << 5 | OK | YES-CERN/GENT | RE43-077-23082013-1410h.plw |  |  | Aug end 13
148 | RE43-078-23082013-1620h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.36 << 5 | OK | YES-CERN/GENT | RE43-078-23082013-1620h.plw |  |  | Aug end 13
149 | RE43-078-26082013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.30 << 5 | OK | YES-CERN/GENT | RE43-078-26082013-1030h.plw |  |  | Aug end 13
150 | RE43-079-26082013-1320h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.32, 0.14 ,0.16 << 5 | OK | YES-CERN/GENT | RE43-079-26082013-1320h.plw |  |  | Aug end 13
151 | RE43-081-27082013-1300h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.02, 0.20, 1.3 << 5 | OK | YES-CERN/GENT | RE43-081-27082013-1300h.plw |  |  | Aug end 13
152 | RE43-082-27082013-1700h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 2.10 << 5 | OK | YES-CERN/GENT | RE43-082-27082013-1700h.plw |  |  | Aug end 13
153 | RE43-082-28082013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.02, 0.02 << 5 | OK | YES-CERN/GENT | RE43-082-28082013-1020h.plw |  |  | Aug end 13
154 | RE43-083-28082013-1300h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.30, 0.29 << 5 | OK | YES-CERN/GENT | RE43-083-28082013-1300h.plw |  |  | Aug end 13
155 | RE42-051-22052013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16,0.12,0.45 << 5 | OK | BARC | RE42-051-22052013-1020h.plw |  |  | Aug end 13
156 | RE42-052-22052013-1340h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26,0.24,0.07<< 5 | OK | BARC | RE42-052-22052013-1340h.plw |  |  | Aug end 13
157 | RE42-053-12082013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.23, 0.64, 0.37 << 5 | OK | YES-CERN | RE42-053-12082013-1100h.plw |  |  | Aug end 13
158 | RE42-055-16082013-1600h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.21,0.23 << 5 | OK | BARC | RE42-055-16082013-1600h.plw |  |  | Aug end 13
159 | RE42-055-19082013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.09 << 5 | OK | BARC | RE42-055-19082013-1000h.plw |  |  | Aug end 13
160 | RE42-054-19082013-1230h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.34, 0.21, 0.22 << 5 | OK | YES-CERN | RE42-054-19082013-1230h.plw |  |  | Aug end 13
161 | RE42-056-19082013-1530h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.21, 0.19, 0.20 << 5 | OK | YES-CERN | RE42-056-19082013-1530h.plw |  |  | Aug end 13
162 | RE42-057-20082013-0930h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.32, 0.04 << 5 | OK | YES-CERN | RE42-057-20082013-0930h.plw |  |  | Aug end 13
163 | RE42-058-20082013-1150h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16, 0.25, 0.50 << 5 | OK | YES-CERN | RE42-058-20082013-1150h.plw |  |  | Aug end 13
164 | RE42-059-20082013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.25, 0.23, 0.17 << 5 | OK | YES-CERN | RE42-059-20082013-1400h.plw |  |  | Aug end 13
165 | RE42-060-21082013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.12, 0.13 << 5 | OK | YES-CERN | RE42-060-21082013-0940h.plw |  |  | Aug end 13
166 | RE42-061-21082013-1350h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.21, 0.36, 0.13 << 5 | OK | YES-CERN | RE42-061-21082013-1350h.plw |  |  | Aug end 13
167 | RE42-062-21082013-1650h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.30, 0.35, 0.13 << 5 | OK | YES-CERN | RE42-062-21082013-1650h.plw |  |  | Aug end 13
168 | RE42-063-22082013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.18, 0.20 << 5 | OK | YES-CERN | RE42-063-22082013-0950h.plw |  |  | Aug end 13
169 | RE43-080-26082013-1700h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.17 << 5 | OK | YES-CERN/GENT | RE43-080-26082013-1700h.plw |  |  | Oct end 13
170 | RE43-080-27082013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.32, 0.30 << 5 | OK | YES-CERN/GENT | RE43-080-27082013-1030h.plw |  |  | Oct end 13
171 | RE43-084-29082013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15, 0.19, 0.10 << 5 | OK | YES-CERN/GENT | RE43-084-29082013-1430h.plw |  |  | Oct end 13
172 | RE43-085-30082013-1050h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.10, 0.09, 0.08 << 5 | OK | YES-CERN/GENT | RE43-085-30082013-1050h.plw |  |  | Oct end 13
173 | RE43-086-02092013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.28, 0.13 << 5 | OK | YES-CERN/GENT | RE43-086-02092013-0940h.plw |  |  | Oct end 13
174 | RE43-087-04092013-1150h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.80, 0.75, 0.70 << 5 | OK | YES-CERN/GENT | RE43-087-04092013-1150h.plw |  |  | Oct end 13
175 | RE43-088-04092013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.18, 0.15, 0.18 << 5 | OK | YES-CERN/GENT | RE43-088-04092013-1410h.plw |  |  | Oct end 13
176 | RE43-089-05092013-1450h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.19, 0.17 << 5 | OK | YES-CERN/GENT | RE43-089-05092013-1450h.plw |  |  | Oct end 13
177 | RE43-090-06092013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.22, 0.17, 0.17 << 5 | OK | YES-CERN/GENT | RE43-090-06092013-1410h.plw |  |  | Oct end 13
178 | RE43-091-07092013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15, 0.16 << 5 | OK | YES-CERN/GENT | RE43-091-07092013-1040h.plw |  |  | Oct end 13
179 | RE43-091-10092013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11 << 5 | OK | YES-CERN/GENT | RE43-091-10092013-0940h.plw |  |  | Oct end 13
180 | RE43-092-10092013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.31, 0.29 << 5 | OK | YES-CERN/GENT | RE43-092-10092013-1400h.plw |  |  | Oct end 13
181 | RE43-092-11092013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12 << 5 | OK | YES-CERN/GENT | RE43-092-11092013-0940h.plw |  |  | Oct end 13
182 | RE43-093-19092013-1120h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.10, 0.11, 0.13 << 5 | OK | YES-CERN/GENT | RE43-093-19092013-1120h.plw |  |  | Oct end 13
183 | RE43-094-19092013-1550h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15, 0.13 << 5 | OK | YES-CERN/GENT | RE43-094-19092013-1550h.plw |  |  | Oct end 13
184 | RE43-094-20092013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14 << 5 | OK | YES-CERN/GENT | RE43-094-20092013-0950h.plw |  |  | Oct end 13
185 | RE43-095-20092013-1130h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.18, 0.15 << 5 | OK | YES-CERN/GENT | RE43-095-20092013-1130h.plw |  |  | Oct end 13
186 | RE43-096-20092013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.20, 1.94 << 5 | OK | YES-CERN/GENT | RE43-096-20092013-1410h.plw |  |  | Oct end 13
187 | RE43-097-23092013-1110h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.40, 0.29, 0.32 << 5 | OK | YES-CERN/GENT | RE43-097-23092013-1110h.plw |  |  | Oct end 13
188 | RE43-098-23092013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.19, 0.19 << 5 | OK | YES-CERN/GENT | RE43-098-23092013-1440h.plw |  |  | Oct end 13
189 | RE43-098-24092013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.17 << 5 | OK | YES-CERN/GENT | RE43-098-24092013-1000h.plw |  |  | Oct end 13
190 | RE43-099-24092013-1140h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.22, 0.12 << 5 | OK | YES-CERN/GENT | RE43-099-24092013-1140h.plw |  |  | Oct end 13
191 | RE43-100-25092013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.27, 0.17 << 5 | OK | YES-CERN/GENT | RE43-100-25092013-0940h.plw |  |  | Oct end 13
192 | RE43-101-25092013-1530h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.24 <<5 | OK | YES-CERN/GENT | RE43-101-25092013-1530h.plw |  |  | Oct end 13
193 | RE43-101-26092013-0930h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.18 << 5 | OK | YES-CERN/GENT | RE43-101-26092013-0930h.plw |  |  | Oct end 13
194 | RE43-102-26092013-1320h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.18, 0.13, 0.41 << 5 | OK | YES-CERN/GENT | RE43-102-26092013-1320h.plw |  |  | Oct end 13
195 | RE42-064-22082013-1330h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.19, 0.23, 0.15 << 5 | OK | YES-CERN | RE42-064-22082013-1330h.plw |  |  | Dec mid 13
196 | RE42-065-22082013-1600h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.26, 0.20, 0.21 << 5 | OK | BARC | RE42-065-22082013-1600h.plw
197 | RE42-066-06112013-1620h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16<<5 | OK | BARC | RE42-066-06112013-1620h.plw
198 | RE42-066-07112013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16, 0.13 << 5 | OK | BARC | RE42-066-07112013-1020h.plw
199 | RE42-067-11112013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.13, 0.11, 0.14 << 5 | OK | YES-CERN | RE42-067-11112013-1000h.plw |  |  | Dec mid 13
200 | RE42-068-12112013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.11, 0.12 << 5 | OK | YES-CERN | RE42-068-12112013-1020h.plw |  |  | Dec mid 13
201 | RE42-069-12112013-1630h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12 << 5 | OK | YES-CERN | RE42-069-12112013-1630h.plw |  |  | Dec mid 13
202 | RE42-069-13112013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.11 << 5 | OK | YES-CERN | RE42-069-13112013-0940h.plw |  |  | Dec mid 13
203 | RE42-070-13112013-1250h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.11, 0.12 << 5 | OK | BARC | RE42-070-13112013-1250h.plw
204 | RE42-071-14112013-0930h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.12, 0.12 << 5 | OK | YES-CERN | RE42-071-14112013-0930h.plw |  |  | Dec mid 13
205 | RE42-072-18112013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.12, 0.12 << 5 | OK | BARC | RE42-072-18112013-1040h.plw
206 | RE42-073-19112013-1120h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15, 0.18, 0.18 << 5 | OK | YES-CERN | RE42-073-19112013-1120h.plw |  |  | Dec mid 13
207 | RE42-075-22112013-1120h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.12, 0.14 << 5 | OK | YES-CERN | RE42-075-22112013-1120h.plw |  |  | Dec mid 13
208 | RE42-076-25112013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.24, 0.76 << 5 | OK | YES-CERN | RE42-076-25112013-0950h.plw |  |  | Dec mid 13
209 | RE42-77-25112013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.11, 0.39 << 5 | OK | YES-CERN | RE42-77-25112013-1410h.plw |  |  | Dec mid 13
210 | RE42-77-26112013-0930h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12 << 5 | OK | YES-CERN | RE42-77-26112013-0930h.plw |  |  | Dec mid 13
211 | RE42-074-26112013-1030h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.70, 0.41, 0.25 << 5 | OK | YES-CERN | RE42-074-26112013-1030h.plw |  |  | Dec mid 13
212 | RE42-078-26112013-1410h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15, 0.17, 0.22 << 5 | OK | YES-CERN | RE42-078-26112013-1410h.plw |  |  | Dec mid 13
213 | RE42-079-27112013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.75, 0.27, 0.15 << 5 | OK | YES-CERN | RE42-079-27112013-0950h.plw |  |  | Dec mid 13
214 | RE42-080-27112013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.30, 0.14, 0.13 << 5 | OK | YES-CERN | RE42-080-27112013-1400h.plw |  |  | Dec mid 13
215 | RE42-081-29112013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.12, 0.14 << 5 | OK | YES-CERN | RE42-081-29112013-1000h.plw |  |  | Dec mid 13
216 | RE42-082-29112013-1440h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.33, 0.17, 0.16 << 5 | OK | YES-CERN | RE42-082-29112013-1440h.plw |  |  | Dec mid 13
217 | RE42-083-12122013-1540h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.15 <<5 | OK | YES-CERN | RE42-083-12122013-1540h.plw |  |  | Jan mid 14
218 | RE42-083-13122013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.21 << 5 | OK | YES-CERN | RE42-083-13122013-0950h.plw |  |  | Jan mid 14
219 | RE42-084-03122013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16, 0.87, 0.11 << 5 | OK | YES-CERN | RE42-084-03122013-0940h.plw |  |  | Jan mid 14
220 | RE42-085-04122013-1100h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.37, 0.52, 0.14 << 5 | OK | YES-CERN | RE42-085-04122013-1100h.plw |  |  | Jan mid 14
221 | RE42-086-04122013-1640h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15 << 5 | OK | YES-CERN | RE42-086-04122013-1640h.plw |  |  | Jan mid 14
222 | RE42-086-05122013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16, 0.16 << 5 | OK | YES-CERN | RE42-086-05122013-1000h.plw |  |  | Jan mid 14
223 | RE42-087-06122013-0940h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.17, 0.31, 0.16 << 5 | OK | YES-CERN | RE42-087-06122013-0940h.plw |  |  | Jan mid 14
224 | RE42-088-06122013-1420h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.24 << 5 | OK | YES-CERN | RE42-088-06122013-1420h.plw |  |  | Jan mid 14
225 | RE42-088-09122013-1400h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.16, 0.44 << 5 | OK | YES-CERN | RE42-088-09122013-1400h.plw |  |  | Jan mid 14
226 | RE42-089-10122013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.4, 0.16, 0.51 << 5 | OK | YES-CERN | RE42-089-10122013-1040h.plw |  |  | Jan mid 14
227 | RE42-090-10122013-1550h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.17 << 5 | OK | YES-CERN | RE42-090-10122013-1550h.plw |  |  | Jan mid 14
228 | RE42-090-12122013-1140h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.44, 0.19 << 5 | OK | YES-CERN | RE42-090-12122013-1140h.plw |  |  | Jan mid 14
229 | RE42-091-16122013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.42, 0.37, 0.26 << 5 | OK | YES-CERN | RE42-091-16122013-1000h.plw |  |  | Jan mid 14
230 | RE42-092-16122013-1430h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 1.09, 0.81, 0.68 << 5 | OK | YES-CERN | RE42-092-16122013-1430h.plw |  |  | Jan mid 14
231 | RE42-093-17122013-1050h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.33, 0.30, 0.28 << 5 | OK | BARC | RE42-093-17122013-1050h.plw
232 | RE42-094-17122013-1520h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.14, 0.20 << 5 | OK | BARC | RE42-094-17122013-1520h.plw
233 | RE42-094-18122013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.15 << 5 | OK | BARC | RE42-094-18122013-1020h.plw
234 | RE42-095-19122013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.12, 0.25, 0.86 << 5 | OK | BARC | RE42-095-19122013-0950h.plw
235 | RE42-096-20122013-1040h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.20, 0.32, 0.60 << 5 | OK | BARC | RE42-096-20122013-1040h.plw
236 | RE42-097-23122013-1000h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.46, 0.25, 0.16 << 5 | OK | BARC | RE42-097-23122013-1000h.plw
237 | RE42-098-24122013-1020h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.33, 0.55, 0.59 << 5 | OK | BARC | RE42-098-24122013-1020h.plw
238 | RE42-099-30122013-0950h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.39, 0.49, 0.13 << 5 | OK | BARC | RE42-099-30122013-0950h.plw
239 | RE42-100-31122013-1150h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.50, 0.38, 0.95 << 5 | OK | BARC | RE42-100-31122013-1150h.plw
240 | RE42-101-01012014-1010h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.29, 0.17, 0.17 << 5 | OK | BARC | RE42-101-01012014-1010h.plw
241 | RE42-102-02012014-1010h.plw | closed | Brass ferrules, crimped properly, In required length, | Hi-Tech |  |  | 0.19, 0.26, 0.21 << 5 | OK | BARC | RE42-102-02012014-1010h.plw