|  | EUROPEAN ORGANIZATION FOR NUCLEAR RESEARCH COMPACT MUON SOLENOID EXPERIMENT |  |
| --- | --- | --- |
| Gas leak test report |  |  |

| IDENTIFICATION |  |
| --- | --- |
| Date | 08.03.2005 |
| Barrel / Endcap ID | YE-1 |
| Circuit System | ME manifold and cooling circuits |
| Test preformed by | Soteb |
| CERN representative supervising | Lasse Isaksen |
| Initial test pressure | 14 bar |
| Time test pressure maintained | 22 Hours 43 min |
| Pressure drop during test period | 1300 mbar |
| Pressure drop during 1 hour | 58.06 mbar/hour |
| Volume | 230 liter |
| Leak rate with temperature correction | 3.72 mbar*l/sec |

| DECISION |  |  |  |
| --- | --- | --- | --- |
| DECISION |  |  |  |
| Contractors decision |  | Requester’s decision |  |
| Reject Approved |  | Rejected Approved |  |
| Name |  | Name |  |
| Date |  | Date |  |

Summary:

Test was preformed once with no correction of leaks.

Figure.1: Capture of computer screen at end of test.

Figure.2: Graph created from test data.

| Leak test ME cooling YE-1 |  |  |
| --- | --- | --- |
| fuite 0.05806 bars par heure |  |  |
| 1.302 bars en 22.43 heures |  |  |
| Key data in stabil time zone |  |  |
| Max temp Haute |  |  |
| Min temp Haute |  |  |
| Delta T |  |  |
| Max temp Bas |  | 25.957886 |
| Min temp Bas |  | 25.477226 |
| Delta T |  | 0.48066 |
| Max press bar |  | 14.318 |
| Min press bar |  | 13.685625 |
| Delta bar |  | 0.631875 |
| Delta mbar |  | 631.875 |
| Volume liter |  | 230 |
| Time in stabile Zone h |  | 11 |
| Total time test h |  | 22.40 |
| Leak rate stable time zone mbar*l/sec |  | 3.670 |
| Leak rate total test time mbar*l/sec |  | 3.717 |
| Max press bar total test time |  | 14.8959375 |
| Min press bar total test time |  | 13.59281 |
| Delta P bar total test time |  | 1.3031 |
| Delta P mbar total test time |  | 1303.125 |
| T1, Start temp in stable zone |  | 298.50927 |
| T2, End temp in stable zone |  | 298.541313 |
| Temp correction factor T2/T1 |  | 1.000107343 |
| Leak rate with temp correction |  | 3.717149341 |

Table.1: Data used for calulation.