## Slide 1: Ambient P5 UXC
2 Nov 2015
All plots are taken over 10 days duration unless otherwise stated

## Slide 2
RB Temperatures

## Slide 3
RE Temperatures

## Slide 4
Abs Pressure differences surface & caverns
4 mbar difference maintained between USC & UXC so avoiding contamination

## Slide 5
Ambient temp UXC55 cavern

## Slide 6
Ambient RH UXC55 cavern
RH is low as the temperatures on the surface are low.

## Slide 7
RE1/1 chambers Temperatures.
Temp. very cool & stable at 19degC
Time since Jan 2010

## Slide 8
RE+1/2/01 Temp. 20.9degC
RE+1/2/25 Temp. 20.4degC
RE+1/2/31 Temp. 22.4degC
RE+1/2/19 Temp. 21.6degC
RE+1/2/13 Temp. 21.2degC
RE+1/2/07 Temp. 20.6degC

## Slide 9
RE+1/3/03?? Temp. 18.9degC
RE+1/3 only one sensor is logged with an incorrect name RE+1/1/03
RE+1/3 Temperatures

## Slide 10
RE+2/2/06 Temp. 20.4degC
RE+2/2/12 Temp. 20.5degC
RE+2/2/16 Temp. 20.3degC
RE+2/2/24 Temp. 19.3degC
RE+2/2/32 Temp. 19.0degC
RE+2/2/36 Temp. 20.1degC
Cooler temps in the Near bottom region

## Slide 11
RE+2/2 & 3 Temp. FOS not available

## Slide 12
RE+2/3/16 Temp. 20.3degC
RE+2/3/024 Temp. 19.3degC
RE+2/3/32 Temp. 19.0degC
Wrong naming RE2/2 rather than RE3/2
RE+2/3/36 Temp. 20.1degC
RE+2/3/06 Temp. 20.1degC
RE+2/3/12 Temp. 20.4degC
Cooler temps in the Near bottom region

## Slide 13
RE+3/2/01 Temp. 21.5degC
RE+3/2/07 Temp. 21.7degC
RE+3/2/13 Temp. 21.5degC
RE+3/2/19 Temp. 21.4degC
RE+3/2/25 Temp. 20.2degC
RE+3/2/31 Temp. 19.2degC
Cooler temps in the Near bottom region

## Slide 14
RE+3/3/13 Temp. 21.5degC
Wrong naming RE3/2 rather than RE3/3
RE+3/3/19 Temp. 21.4degC
RE+3/3/07 Temp. 21.1degC
RE+3/3/01 Temp. 20.4degC
RE+3/3/31 Temp. 19.4degC
RE+3/3/25 Temp. 20.2degC

## Slide 15
RE+3/3/1-6 Temp. 19.2-20.7degC
FOS temp Sensors

## Slide 17
Temperatures. Wheel Zero Sector 12

## Slide 18
Wheel 0 Sector 8

## Slide 19
We have lost RE+3, instead it is marked RE-4

## Slide 20
Temp drop on Sunday ?
UXC55 Ambient Temperature

## Slide 21
YE+1 also see the Sunday drop in Temperature between the yokes.

## Slide 22
Individual FOS temperatures. Only one shows the temp. drop.
RE+2 FOS sensors

## Slide 24
Coolant temperature RE+2

## Slide 25: Conclusion
Stable temperatures.
The temperature in RE+3 is still missing
Pressure between cavern maintained, safety reasons.
There are 2 temperatures on each RE1/1, only reading one !
RE+1/3 only one of 6 temp. sensors are logged !
RE+2/2 & 2/3 individual plots FOS not available.
RE+2 & 3 Temperatures are lowest in the near bottom region.
RE- will be looked at for next week.