## Type 1
General Information
Experiment | CMS |  | Target Leak flow at reference conditions | <1*10-3 STD cc/s
Sub-detector | RPC
Module | Distibution
Rack | Barrel Level 0
Test Method: | Pressure decay method.
Persons performing test:
Location of Test
Leak test parameter
| Start |  | End |  | Difference
Time | 2007-09-03 09:00 |  | 2007-09-03 09:10 |  | 600 | sec
Pressure Inside | 0.975 | bara | 0.97 | bara | 0.005 | bara
Pressure outside | 0.97 | bara | 0.97 | bara | 0 | bara
Delta P | 0.005 | bara | 0 | bara | 0.005 | bara
Temperature | 296.6 | K | 296.6 | K | 0 | K
Volume | 26000 | cm3
Results
Leak at test conditions | 0.19943 | Std cc/s | Leak rate conform to specification |  | no
Leak flow at reference conditions | 62.9302 | Std cc/s
measured pressure drop