| CERN reference N° | ### SCEM 04.71.06.400.0 |
| --- | --- |
| ## Identification | Twisted pair rouNd câble |

| REQUIREMENTS |  |
| --- | --- |
| Applicable documents | IEC60332-3-2 ; IEC60754-2 ; IEC61034 ; CERN IS23 |
| Mechanical properties | Core : Stranded tinned copper, Section : AWG28/7 or AWG26/7 Insulation : High density polyethylene, LSZH. Individual conductor AND insulation must be suitable for IDC type connector of 1.27mm pitch. Diameter 0.7mm is common to some cables. Pairs : Each group of 4 pairs white/blue; white/orange; white/green / white brown Lay-up : Pairs twisted in 5 groups of 4 pairs, diameter over assembly 3,10mm Screen : Al-PET-foil on the total and glass fibre as flame barrier + tinned copper braid, coverage > 75% Outer sheath : Thermoplastic LSZH flame retardant compound – Blue RAL 5015 Max. outer diameter : 10mm “Manufacturer logo – CERN 04.71.06.400.0 – Zero halogen – IEC60332-1 – Manufacturing date – Calibration in meter” |
| Electrical properties | Insulation resistance : >1000MOhm.km Capacitance : <49pF/m Velocity of propagation : ca 58% Characteristic impedance : 110Ohm +- 10Ohm (f ≥1MHz - 100MHz) Propagation delay : <460ns/100m Skew time between pairs : <1ns/25m Test voltage : 1kV, DC, 1min, core/core and core/screen |
| Operating voltage Operating temperature | 150Vrms -65 to 70°C |

ACCORDING TO CERN SAFETY INSTRUCTION IS23

04.71.06.400.0 – not to scale !