RPC Endcap		Station 3

- Cooling Services 	Chambers grouped in 20sectors

| RPC | Nos. Chamber Station | Nos. FEB /chamber | Nos. LB /20 | Total Heat Dissipation /20(Watts) (FEB +LB) | Pipes /20 | Section /20 (cm2) 8mm | Total Nos. Pipes | Section Leaving Yoke cm2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RE3/1 | 18 | 4 | 1 1/3 | 10.3 + 4 = 14.3 |  |  |  |  |
| RE3/2 | 36 | 3 | 2 | (15.4+ 6) =21.4 |  |  |  |  |
| RE3/3 | 36 | 3 | 2 | (15.4 + 6) =21.4 |  |  |  |  |
| Total | 90 |  |  | 57.1 | 2 | 1.28 | 36 |  |
| Total/ Station/ Endcap | 90 |  |  | 1027.8 Watts | 36 |  | 36 | 2x12 =2.9 |

# Pipe ext. 8mm up to Yoke periphery.

Distribution on Yoke periphery pipe is 38 exterior

Heat dissipation from FEB is 80mW/ch. (= 2.56W/FEB) for 32 channels FEB

Heat dissipation from LB is 3W/LB

Section is 2 in cm2

IMC 11.2000