CONSTRUCTION DETAILS

2x0,22

Conductor     	: 	nomin. sect.   0.22 mm2 tinned copper 7X0,20 mm

conductor diameter 0.60 mm

Insulation    	: 	High density polyethylene LSZH thickness 0.20 mm

Colours t.b.a., nominal diameter   	1.0 mm

Pair	:	conductors twisted in pair

2x2,5

Conductor     	: 	nomin. sect.   2.50 mm2 bare copper 48X0,25 mm

conductor diameter 	2.00 mm

Insulation    	: 	LDPE polyethylene LSZH colours red and black

thickness 0,5 mm,  nominal diameter 	3.0 mm

Assembly      	: 	2x2,5+1x2x0.22 twisted together with F.R. LSZH filler

diameter over assembly 	6.0 mm

Overall Shield 	: 	Aluminium/polyester tape with 7X0,20 mm tpc drain wire

in contact with tinned copper braid wire diameter 0.10 mm

minimum coverage 85%

nominal diameter	6.90 mm

Outer sheath   	: 	Thermoplastic LS0H flame retardant compound blue RAL 5015

thickness 0,9 mm, nominal diameter 8.30 mm

Marking	: 	NOVACAVI + to be advised

------------------------------------------------------------

ELECTRICAL AND PHYSICAL CHARACTERISTICS

Electrical resistance sect.: 0.22 < 88.636 ohm/km at 20°C

Electrical resistance sect.: 2.50 <  7.980 ohm/km at 20°C

Insulation resistance   >    1000 Mohm x km at 20° C

Test voltage cond./cond:	1000 V ac x1 min.

Test voltage cond./shield:	500 V ac x1 min.

OTHER CHARACTERISTICS

Weight :   130 kg/km

Bending radius static minimum   :   45 mm

Working temperature range       : from   -30 to +70   °C

REFERENCE STANDARDS

IEC 60332-1, CERN IS 23 excluding radiation resistance for sheath