Calculations for the heat Transfers within the Front End Board and its cooling system

Used on the CMS Endcap RPC’s

# Assumptions

3 Watts/ FEB

20 sector consisting of 5 chambers (pipe length of 34m)

All electrical power is disipated into the copper sheet

The cooling water temp is assumed to be at Tm = 20C

`

We wish to optimise the heat transfer  coefficient so turbulent conditions are required. A reasonable flow rate of 1m/s can be taken.

The cooling system within one chamber consists of a continuace piece of 8 x 6mm copper pipe with bends having a radius > 3x the diamiter (30mm)

Flowing water off the periferal manifold.

Thus a good estimation is given by:

The Mas flow is given by

M⋅MM

ΔP=ρ.λ.LDh.c22

Mass Flow

We want to achieve both a high heat transfer coefficient (h) through turbulent flow , a reasonable velocity and a pressure drop less than that available and we need to minimize the T increase of the water ciculating through a sector in order to be able to pick-up the low temperature heat sources.

Choosing  a T of 0.5C  for the sector of 20 dissipating 20Watts from the FEB’s

M[kgs]=QCp⋅ΔT

= 28.7  [g. s-1]

# Velocity of the Flow

M=VρM=A[m2]⋅c[m⋅s−1]⋅ρ[kg⋅m3]∴c=1.014[m⋅s−1]

Reynolds Number

We have 8 x 6mm pipe , D = 0.006m and  as the Dynamic Viscosity

Re=4⋅Mπ⋅D⋅μ=6082

According to Moody we are now out side the Laminar region and Critical zone  but not yet fully turbulent. This is the Transition Zone.

Now we can estimate the Pressure drop over one sector circuit L = 34m

ΔP=ρ⋅λ⋅L⋅c2D⋅2

=1.04Bar

Nota. This is for bends of radius .> 3 x pipe diam. And includes no valves or unions.

This is well with in the operational conditions of the Peripheral manifold

11-8 Bar

Empirical correlations are needed to understand the thermal transfer into the coolant.

The Dittus-Boelter equation says

Nu=0.023⋅Re45⋅Pr0.452.6

for transfering heat to the internal fluid. Errors of up to 25% can result from this simple correlation.

According to Gnielinski the above can be improved for 3000 < Re < 5 x 106 and 0.5 < Pr < 2000

Nu=(f8)⋅(Re−1000)⋅Pr1+12.7⋅(f8)12(Pr23−1)

I have not used this at this stage of the estimation.

The Heat Transfer Coefficient ;

h=Nu⋅kD

= 5242 [ W.m-2.K-1]

This is a good result because the peak value of “h” is at the onset of fully turbulent flow.

Using Newton’s Law of Cooling;

q=h(Ts−T∞)∴ΔT=0.15°C