## Sheet1
Chiller for the study of GE1/1 electronics
[7 empty] | Ian Crotty |  | 2014-12-04
Company Name | Model | Cooling capacity @ 20degC | Temp Constance | flow rate | Pressure | Cost |  | Fits Spec ?
|  |  | ± |  |  |  |  | Detail study | 40deg Mock up
|  | [kW] | [degC] | [l/min] | [Bar] | [chf]
Specification
| Detailed study | > 0.2 | <0.05 | >5 | >0.2
| Mock up | >0.4 | ~0.5 | >2 | >2
Huber
| CC-K25 | 0.4 | 0.02 | 27 | 0.7 | 6251 |  | Yes | No
Julabo
| FL1203 | 1.2 | 0.5 | 10 | 2.8 | 5350 |  | No | yes
| FP51-SL HSP | 2 | 0.05 | 22-26 | 0.4-0.7 | 11132 |  | just | yes * | Requires ext pump
| Presto A30 | 0.5 | 0.05 | 25 | 0.5 | 8764 |  | just | yes * | Requires ext pump
VWR | Cryo-compact CF30 | 0.32 | 0.03 | 15 | 0.35 | 4405 |  | just | No
05.12.2014 | F32_HL | 0.45 | 0.01 | 22-26 | 0.4-0.7 | 6333 |  | yes | No
| F25-HE | 0.26 | 0.01 | 22-26 | 0.4-0.7 | 5257 |  | yes | No
| F25-ME | 0.26 | 0.01 | 11-16 | 0.23-0.45 | 4497 |  | yes | No
Lauda
| Alpha RA8 | 0.225 | 0.05 | 15 | 0.2 | 3713 |  | just | No
| Proline RP 1840C Ed X | 0.9 | 0.01 | 27 | 0.7 | 9838 |  | yes | Yes * | Requires ext pump
Betta-Tech Controls | CU-500 with Mod | 1.275 | 0.5 | 5.2 | 3 | 4500 |  | No | yes
| CU-500 with Mod | 1.275 | 0.2? | 5.2 | 3 | 4900 |  | No | yes
Conclusion
| The Huber is ok for the detailed study but has the next to lowest power. |  |  |  |  | It does not fit the spec for the Mock-up
The Julabo FL1203 fits the spec for the mock-up with no modifications
The Julabo F32HL has good cooling capacity a high P for the range and a excellent temp stability for the edetailed study.