## Versioning
2016-02-02 | Original file by Armando
2016-02-05 | Modification by PT to split Rack and Encap cooling circuit power/flow
2016-02-09 | Data updated for RPC (mail of Salvatore)
2017-07-19 | Upgrade needs added on Micha input
2017-07-20 | Micha input on details for CSC, Andrey input on GEMs
2018-11-13 | Input of Michele & C. on new power dissipations GEMs & ME0 - Paola taking out non-muon powers for LS3
2018-11-14 | P. Tropea summary update
2018-11-22 | P. Tropea update with RPC chamber power dissipation (10 W/chamber for present chambers, 20 W/chamber for RE3/1 and RE4/1) and GEM "high flow" request for LS3
Added RBX power dissipation
Changed naming for cable trays cooling which was called "HE" and is now "EE"
2018-12-04 | P. Tropea change of GEM flow for LS2 as from M. Bianco request
2018-12-14 | Inputs from Muon subsystems

## Summary
YE+1 and YE-1 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-LS2 | LS3 constant flow
Total flow-disk manifold | liter/min | 740.8 | 798.8 | 58 | 740.8 | 730.8 | -10 | 740.8
| m3/h | 44.448 | 47.928 | 3.48 | 44.448 | 43.848 |  | 44.448
Total Heat removed | kW | 72.996 | 89.28 | 16.284 | 89.28 | 66.312 | -22.968 | 66.312
Total temperature rise | C | 1.4144 | 1.6043 |  | 1.7299 | 1.3025 |  | 1.2849
YE+2 and YE-2 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow
Total flow | liter/min | 0 | #REF! | #REF! | 0 | #REF! | #REF! | 0
| m3/h | 0 | #REF! | #REF! | 0 | #REF! |  | 0
Total Heat removed | kW | 0 | 63.424 | 63.424 | 63.424 | 63.424 | 63.424 | 63.424
Total temperature rise | C | #DIV/0! | #REF! |  | #DIV/0! | #REF! |  | #DIV/0!
YE+3 & YE-3 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow
Total flow | liter/min | 397.6 | 454 | 56.4 | 397.6 | 454 | 56.4 | 397.6
| m3/h | 23.856 | 27.24 | 3.384 | 23.856 | 27.24 |  | 23.856
Total Heat removed | kW | 40.452 | 46.824 | 6.372 | 46.824 | 46.824 | 6.372 | 46.824
Total temperature rise | C | 1.4604 | 1.4804 |  | 1.6904 | 1.4804 |  | 1.6904
Flow-Heat Summary for full circuit
ENDCAP circuit for 6 disks |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow | Measures '17/'18
Total flow | liter/min | 1138.4 | #REF! | #REF! | 1266.6667 | #REF! | #REF! | 1266.6667 | 1266.6667
| m3/h | 68.304 | #REF! | #REF! | 76 | #REF! | #REF! | 76 | 76
Total Heat removed | kW | 113.448 | 199.528 | 86.08 | 199.528 | 176.56 | 63.112 | 176.56 | 137
Total temperature rise | C | 1.4305 | #REF! |  | 2.2611 | #REF! |  | 2.0008 | 1.5525
Disk flow rate | liter/min | 72 | The disk cooling circuit is fed with potentially 4 m3/h, a test in LS2 shall be done to verify the numbers and see the impact of closing such circuits on the overall muon chamber temperature
| m3/h | 4.32
RACK CIRCUIT - same for YE+1 & YE-1 |  | Nominal
Total flow-tower manifold | liter/min | 182.4 |  |  | 1266.6667
Total Heat removed | kW | 28.2 |  |  | 76
Total temperature rise | C | 2.2192 |  |  | 190
2.1531
Note on J23: paola tropea: From EN-CV flowmeter
Note on J24: paola tropea: Calculated from DT and Flow measurements
Note on J25: paola tropea: From main circuit T readings

## Present YE1
YE1 cooling parameters
| ENDCAP COOLING CIRCUIT | [15 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | GEM cooling circuit GE1/1- demostrator | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1 | RPC cooling circuit RE2 | RBX | VME/CRB circuit (minirack) | Disk circuit | EE cable tray/link boards | EE cable tray | LV periphery cable tray | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 370.4 | 2.3 | 2.3 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 2 | 4 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.4188 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 133254.6915 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber | W |  | 86 | 105 | 270 | 45 | 10 | 10 | 12 | 10 | 300
# chambers/circuit | # |  | 4 | 4 | 2 | 4 | 6 | 6 | 4 | 4 | 1
Heat removal/circuit | W | 36498 | 344 | 420 | 540 | 180 | 60 | 60 | 48 | 40 | 300 | 852 | 400 | 247 | 147 | 390 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.4144 | 2.1469 | 2.6212 | 1.9378 | 1.2919 | 0.43062 | 0.43062 | 0.3445 | 0.28708 | 2.1531 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 2.5 | 6 | 6 | 1 | 18 | 18 | 6 | 12 | 6 | 30 | 4 | 1 | 8 | 1 | 8
Total flow | lt/min | 369.4 | 20.7 | 20.7 | 72 | 6 | 12 | 12 | Flow not accounted since in series with RBXs | 36 | 36 | 30 | 24 | 24 | 60 | 16 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 36498 | 3096 | 3780 | 9720 | 450 | 360 | 360 | 48 | 720 | 5400 | 5112 |  | 1482 | 4410 | 1560 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [11 empty] | 4800
Pressure drop (measured) | bar | [7 empty] | 1.6? |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 370.4
Total Heat removed | kW | 36.498
Total temperature rise | C | 1.4144
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192
FOR RE1/1: Flow not accounted since in series with RBXs - RE1/1 only on +end

## Upgr YE1 LS2
YE1 UPGRADE cooling parameters | [14 empty] | LS2 | LS21/2 | LS3
| ENDCAP COOLING CIRCUIT | [16 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE2 | RBX | VME/CRB circuit (minirack) | Disk circuit | EE cable tray/link boards | EE cable tray | LV periphery cable tray | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0 | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 8 | 8 | 8 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 6 | 6 | 6 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 28.26 | 28.26 | 28.26 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 399.4 | 2.3 | 2.3 | 4 | 2 | 2 | 2 | 2 | 5 | 2 | 4 | 2 | 4 | 4 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.6082 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 2.359 | 1.1795 | 2.359 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 143687.6992 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 13675.6345 | 6837.8172 | 13675.6345 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber-superchamber | W |  | 86 | 105 | 270 | 10 | 10 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 60
# chambers/circuit |  |  | 4 | 4 | 2 | 6 | 6 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 6
Heat removal/circuit | W | 44640 | 344 | 420 | 540 | 60 | 60 | 40 | 300 | 852 | 400 | 247 | 147 | 390 | 480 | 960 | 360 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.6043 | 2.1469 | 2.6212 | 1.9378 | 0.43062 | 0.43062 | 0.28708 | 2.1531 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 1.7225 | 6.89 | 1.2919 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 18 | 18 | 6 | 12 | 6 | 30 | 4 | 6 | 6 | 18 | 1 | 8 | 1 | 8
Total flow | lt/min | 399.4 | 20.7 | 20.7 | 72 | 12 | 12 | 36 | 36 | 30 | 24 | 24 | 60 | 16 | 24 | 12 | 72 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 44640 | 3096 | 3780 | 9720 | 360 | 360 | 720 | 5400 | 5112 |  | 1482 | 4410 | 1560 | 2880 | 5760 | 6480 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [9 empty] | 4800
Pressure drop (measured) | bar | [8 empty] | 10.5psi/lvps | [5 empty] | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 399.4
Total Heat removed | kW | 44.64
Total temperature rise | C | 1.6043
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192
Changes for LS2
GEM demostrator power is taken out
GE1/1 installed and powered
GE2/1 cooling prepared
RE1/1 goes away and is replaced by GE1/1

## Upgr YE1 LS3
YE1 UPGRADE cooling parameters | [11 empty] | REMOVED |  |  | LS2 | LS3 | LS3
| ENDCAP COOLING CIRCUIT | [16 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE2 | Disk circuit | RBX | VME/CRB circuit (minirack) | EE cable tray/link boards | EE cable tray | LV periphery cable tray | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0 | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 12.7 | 8 | 12.7 | 10 | 10 | 10 | 8 | 8 | 8 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1.24 | 1 | 1.24 | 1 | 1 | 1 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 10.22 | 6 | 10.22 | 8 | 8 | 8 | 6 | 6 | 6 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 81.992 | 28.26 | 81.992 | 50.24 | 50.24 | 50.24 | 28.26 | 28.26 | 28.26 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 365.4 | 2.3 | 2.3 | 4 | 2 | 2 | 2 | 2 | 2 | 5 | 4 | 2 | 4 | 4 | 6 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.3861 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 1.1795 | 0.40654 | 1.1795 | 1.0164 | 1.327 | 0.66348 | 1.327 | 2.359 | 3.5386 | 2.359 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 131455.897 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 6837.8172 | 4014.3741 | 6837.8172 | 10035.9353 | 10256.7258 | 5128.3629 | 10256.7258 | 13675.6345 | 20513.4517 | 13675.6345 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber-superchamber | W |  | 86 | 105 | 270 | 10 | 10 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 40 | 160 | 60
# chambers/circuit |  |  | 4 | 4 | 2 | 6 | 6 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 6 | 6
Heat removal/circuit | W | 33156 | 344 | 420 | 540 | 60 | 60 | 40 | 400 | 300 | 852 | 247 | 147 | 390 | 480 | 960 | 360 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.3025 | 2.1469 | 2.6212 | 1.9378 | 0.43062 | 0.43062 | 0.28708 | 2.8708 | 2.1531 | 2.4459 | 0.88636 | 1.055 | 1.3995 | 1.7225 | 2.2967 | 1.2919 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 18 | 12 | 18 | 6 | 6 | 30 | 4 | 6 | 6 | 18 | 1 | 8 | 1 | 8
Total flow | lt/min | 329.4 | 20.7 | 20.7 | 72 | 12 | 12 | 36 | 24 | 36 | 30 | 24 | 60 | 16 | 24 | 36 | 72 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 33156 | 3096 | 3780 | 9720 | 360 | 360 | 720 |  | 5400 | 5112 | 1482 | 4410 | 1560 | 2880 | 5760 | 6480 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [7 empty] | 4800
Pressure drop (measured) | bar | [9 empty] | 10.5psi/lvps |  |  |  |  | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 365.4
Total Heat removed | W | 33.156
Total temperature rise | C | 1.3025
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192
Changes for LS3
RBX disappear
EE cable tray and LV perifery cable tray go away (need for cable tray cooling for CE taken on rack circuit on Ex EE manifold)

## Present YE2
YE2 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min |  | 2.3 | 2.3 | 2 | 5 | 5 | 10
Flow velocity | m/sec |  | 0.78256 | 0.78256 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless |  | 5972.7244 | 5972.7244 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 109 | 130
# chambers/circuit | # |  | 3 | 3
Heat removal/circuit | W | 0 | 327 | 390 | 400 | 852 | 852 | 2348
Temperature rise | C | #DIV/0! | 2.0408 | 2.434 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 176.8 | 55.2 | 27.6 | 24 | 20 | 10 | 40
Heat removed | W |  | 7848 | 4680 |  | 3408 | 1704 | 9392
Heat removal capacity | W
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 0
Total Heat removed | kW | 0
Total temperature rise | C | #DIV/0!

## Upgr YE2 LS2
YE2 UPGRADE cooling parameters |  |  |  | LS2
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | #REF! | 2.3 | 4 | 2 | 5 | 5 | 10
Flow velocity | m/sec | #REF! | 0.78256 | 1.361 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | #REF! | 5972.7244 | 10387.3467 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 109 | 260 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 3 | 3 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 36512 | 327 | 780 | 400 | 852 | 852 | 2348
Temperature rise | C | #REF! | 2.0408 | 2.799 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 197.2 | 55.2 | 48 | 24 | 20 | 10 | 40
Heat removed | W | 31712 | 7848 | 9360 |  | 3408 | 1704 | 9392
Heat removal capacity | W
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | #REF!
Total Heat removed | W | 31.712
Total temperature rise | C | #REF!
Changes for LS2
CSC double power dissipation and flow requst

## Upgr YE2 LS3
YE2 UPGRADE cooling parameters |  |  |  | LS3
IN LS3 NO CHANGES WITH RESPECT TO LS2 on YE2 | ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | #REF! | 2.3 | 4 | 2 | 5 | 5 | 10
Flow velocity | m/sec | #REF! | 0.78256 | 1.361 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | #REF! | 5972.7244 | 10387.3467 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 109 | 260 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 3 | 3 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 36512 | 327 | 780 | 400 | 852 | 852 | 2348
Temperature rise | C | #REF! | 2.0408 | 2.799 | 2.8708 | 2.4459 | 2.4459 | 3.3703
|  |  | 0 | 0
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 197.2 | 55.2 | 48 | 24 | 20 | 10 | 40
Heat removed | W | 31712 | 7848 | 9360 |  | 3408 | 1704 | 9392
Heat removal capacity | W |  | 0 | 0
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | #REF!
Total Heat removed | kW | 31.712
Total temperature rise | C | #REF!
Changes for LS3
NONE

## Present YE3
YE3 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 198.8 | 2.3 | 2.3 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.0881 | 0.78256 | 0.78256 | 1.1795 | 1.1795 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 90704.4973 | 5972.7244 | 5972.7244 | 6837.8172 | 6837.8172 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 120 | 123 | 10 | 10
# chambers/circuit | # |  | 3 | 3 | 4 | 4
Heat removal/circuit | W | 20226 | 360 | 369 | 40 | 40 |  | 426 | 1000 | 2516
Temperature rise | C | 1.4604 | 2.2467 | 2.3029 | 0.28708 | 0.28708 | 0 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 12 | 4 | 3 | 3
Total flow | liter/min | 198.8 | 27.6 | 13.8 | 36 | 36 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 20226 | 4320 | 2214 | 720 | 720 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [5 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 198.8
Total Heat removed | kW | 20.226
Total temperature rise | C | 1.4604

## Upgrade YE3 LS2
YE3 UPGRADE cooling parameters |  |  |  | Replacement of electronics LS2
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 28 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 227 | 2.3 | 4 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.3843 | 0.78256 | 1.361 | 1.1795 | 1.1795 | 1.2 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 103571.0306 | 5972.7244 | 10387.3467 | 6837.8172 | 6837.8172 | 6838 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 120 | 260 | 10 | 10 | 20 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 3 | 3 | 6 | 4 | 2 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 23412 | 360 | 780 | 60 | 40 | 40 |  | 426 | 1000 | 2516
Temperature rise | C | 1.4804 | 2.2467 | 2.799 | 0.43062 | 0.28708 | 0.2 | 0 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 9 | 12 | 4 | 3 | 3
Total flow | liter/min | 227 | 27.6 | 24 | 36 | 36 | 18 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 23412 | 4320 | 4680 | 1080 | 720 | 360 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [6 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 227
Total Heat removed | kW | 23.412
Total temperature rise | C | 1.4804
Changes for LS2
ME4/1heat per circuit rises to 780 W instead of 370 W
RPC upgrade chambers to be installed btween LS2 and LS3
The RE3/1 cooling is taken off the RE3/2 and RE3/3 system so there is no more flow and a minimal 0.1degC increase
1 chamber more per cooling circuit on RE3 spigots: on table the number of chambers is 6 and not 5 in order to take into account the power dissipation of the RE3/1 chambers which is 20 W instead of 10 as old chambers
The RE4/1 cooling is taken off the mini-manifolds of the other RE4 stations, using "T"s with 9 circuits out of 18 existing, giving a similar temp increase as the RE3 station.
The YE3 manifold flow rate increase is half of the RE3 station namely 18 litres/min on a total of 161 [litres/min] .
Note on F12: Paola Tropea: 1 additional chamber for RE3/1 (new chamber) per each circuit - since new electronics, each has a power of 20 W instead of 10- I note on the column nb of chambers + 2 in order to have the correct power balance

## Upgrade YE3 LS3
YE3 UPGRADE cooling parameters
IN LS3 NO CHANGES WITH RESPECT TO LS2 on YE3 | Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 28 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 227 | 2.3 | 4 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.3843 | 0.78256 | 1.361 | 1.1795 | 1.1795 | 1.2 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 103571.0306 | 5972.7244 | 10387.3467 | 6837.8172 | 6837.8172 | 6838 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 120 | 260 | 10 | 10 | 20 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 3 | 3 | 6 | 4 | 2 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 23412 | 360 | 780 | 60 | 40 | 40 |  | 426 | 1000 | 2516
Temperature rise | C | 1.4804 | 2.2467 | 2.799 | 0.43062 | 0.28708 | 0.2 | 0 | 1.301 | 3.0541 | 3.8016
0
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 9 | 12 | 4 | 3 | 3
Total flow | liter/min | 227 | 27.6 | 24 | 36 | 36 | 18 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 23412 | 4320 | 4680 | 1080 | 720 | 360 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [6 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 227
Total Heat removed | kW | 23.412
Total temperature rise | C | 1.4804
Changes for LS3
NONE
Note on F12: Paola Tropea: 1 additional chamber for RE3/1 (new chamber) per each circuit - since new electronics, each has a power of 20 W instead of 10- I note on the column nb of chambers + 2 in order to have the correct power balance