## Versioning
2016-02-02 | Original file by Armando
2016-02-05 | Modification by PT to split Rack and Encap cooling circuit power/flow
2016-02-09 | Data updated for RPC (mail of Salvatore)
2017-07-19 | Upgrade needs added on Micha input
2017-07-20 | Micha input on details for CSC, Andrey input on GEMs
2018-11-13 | Input of Michele & C. on new power dissipations GEMs & ME0 - Paola taking out non-muon powers for LS3
2018-11-14 | P. Tropea summary update

## Summary
YE+1 and YE-1 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-LS2 | LS3 constant flow
Total flow-disk manifold | liter/min | 672.8 | 734.8 | 62 | 672.8 | 594.8 | -78 | 672.8
| m3/h | 40.368 | 44.088 | 3.72 | 40.368 | 35.688 |  | 40.368
Total Heat removed | kW | 66.28 | 81.56 | 15.28 | 81.56 | 69.392 | -12.168 | 69.392
Total temperature rise | C | 1.4141 | 1.5932 |  | 1.7401 | 1.6746 |  | 1.4805
YE+2 and YE-2 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow
Total flow | liter/min | 305.6 | 346.4 | 40.8 | 305.6 | 346.4 | 40.8 | 305.6
| m3/h | 18.336 | 20.784 | 2.448 | 18.336 | 20.784 |  | 18.336
Total Heat removed | kW | 54.064 | 63.472 | 9.408 | 63.472 | 63.472 | 9.408 | 63.472
Total temperature rise | C | 2.5394 | 2.6301 |  | 2.9813 | 2.6301 |  | 2.9813
YE+3 & YE-3 |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow
Total flow | liter/min | 397.6 | 454 | 56.4 | 397.6 | 454 | 56.4 | 397.6
| m3/h | 23.856 | 27.24 | 3.384 | 23.856 | 27.24 |  | 23.856
Total Heat removed | kW | 43.332 | 49.704 | 6.372 | 49.704 | 49.704 | 6.372 | 49.704
Total temperature rise | C | 1.5644 | 1.5715 |  | 1.7944 | 1.5715 |  | 1.7944
Flow-Heat Summary for full circuit
ENDCAP circuit for 6 disks |  | Nominal | LS2 request | LS2-nominal | LS2 constant flow | LS3 | LS3-nominal | LS3 constant flow | Measures '17/'18
Total flow | liter/min | 1376 | 1535.2 | 159.2 | 1376 | 1395.2 | 19.2 | 1376 | 1266.6667
| m3/h | 82.56 | 92.112 | 9.552 | 82.56 | 83.712 | 1.152 | 82.56 | 76
Total Heat removed | kW | 163.676 | 194.736 | 31.06 | 194.736 | 182.568 | 18.892 | 182.568 | 137
Total temperature rise | C | 1.7074 | 1.8208 |  | 2.0314 | 1.8783 |  | 1.9045 | 1.5525
RACK CIRCUIT - same for YE+1 & YE-1 |  | Nominal
Total flow-tower manifold | liter/min | 182.4
Total Heat removed | kW | 28.2
Total temperature rise | C | 2.2192
Note on J23: paola tropea: From EN-CV flowmeter
Note on J24: paola tropea: Calculated from DT and Flow measurements
Note on J25: paola tropea: From main circuit T readings

## Present YE1
YE1 cooling parameters
| ENDCAP COOLING CIRCUIT | [14 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | GEM cooling circuit GE1/1- demostrator | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 336.4 | 2.3 | 2.3 | 4 | 2 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.1968 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 1.1795 | 2.359 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 121022.8893 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 6837.8172 | 13675.6345 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber | W |  |  |  |  | 200 | 20 | 20 | 25 | ?
# chambers/circuit | # |  |  |  |  | 2 | 6 | 6 | 4 | ?
Heat removal/circuit | W | 33140 | 344 | 420 | 540 | 400 | 120 | 120 | 100 | 80 | 852 | 400 | 247 | 147 | 390 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.4141 | 2.1469 | 2.6212 | 1.9378 | 2.8708 | 0.86124 | 0.86124 | 0.35885 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 2.5 | 6 | 6 | 1 | 18 | 6 | 12 | 6 | 30 | 4 | 1 | 8 | 1 | 8
Total flow | lt/min | 337.4 | 20.7 | 20.7 | 72 | 6 | 12 | 12 | 4 | 36 | 30 | 24 | 24 | 60 | 16 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 33140 | 3096 | 3780 | 9720 | 1000 | 720 | 720 | 100 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [10 empty] | 4800
Pressure drop (measured) | bar | [7 empty] | 1.6? |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 336.4
Total Heat removed | kW | 33.14
Total temperature rise | C | 1.4141
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192

## Upgr YE1 LS2
YE1 UPGRADE cooling parameters | [14 empty] | LS2 | LS21/2 | LS3
| ENDCAP COOLING CIRCUIT | [16 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0 | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 8 | 8 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 6 | 6 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 28.26 | 28.26 | 50.24 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 367.4 | 2.3 | 2.3 | 4 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 2 | 4 | 2 | 4 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.3992 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 2.359 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 1.1795 | 2.359 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 132175.4148 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 13675.6345 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 6837.8172 | 13675.6345 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber-superchamber | W |  | 0 | 0 | 0 | 20 | 20 | 25 | ? | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 60
# chambers/circuit |  |  | 0 | 0 | 0 | 6 | 6 | 4 | ? | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 6
Heat removal/circuit | W | 40780 | 344 | 420 | 540 | 120 | 120 | 100 | 80 | 852 | 400 | 247 | 147 | 390 | 480 | 960 | 360 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.5932 | 2.1469 | 2.6212 | 1.9378 | 0.86124 | 0.86124 | 0.35885 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 3.445 | 3.445 | 1.2919 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 1 | 18 | 6 | 12 | 6 | 30 | 4 | 6 | 6 | 18 | 1 | 8 | 1 | 8
Total flow | lt/min | 367.4 | 20.7 | 20.7 | 72 | 12 | 12 | 4 | 36 | 30 | 24 | 24 | 60 | 16 | 12 | 24 | 72 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 40780 | 3096 | 3780 | 9720 | 720 | 720 | 100 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 2880 | 5760 | 6480 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [9 empty] | 4800
Pressure drop (measured) | bar | [6 empty] | 1.6? |  | 10.5psi/lvps | [5 empty] | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 367.4
Total Heat removed | kW | 40.78
Total temperature rise | C | 1.5932
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192
Changes for LS2
GEM demostrator power is taken out
GE1/1 installed and powered
GE2/1 cooling prepared

## Upgr YE1 LS3
YE1 UPGRADE cooling parameters | [11 empty] | REMOVED |  |  | LS2 | LS3 | LS3
| ENDCAP COOLING CIRCUIT | [16 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0 | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 8 | 8 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 6 | 6 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 28.26 | 28.26 | 50.24 | 1586.8003 | 585.0527 | 1586.8003 | 585.0527
Flow rate | liter/min | 297.4 | 2.3 | 2.3 | 4 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 2 | 4 | 2 | 6 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 1.9421 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 2.359 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 1.1795 | 3.5386 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 106992.2928 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 13675.6345 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 6837.8172 | 20513.4517 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber-superchamber | W |  | 0 | 0 | 0 | 20 | 20 | 25 | ? | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 60
# chambers/circuit |  |  | 0 | 0 | 0 | 6 | 6 | 4 | ? | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 6
Heat removal/circuit | W | 34696 | 344 | 420 | 540 | 120 | 120 | 100 | 80 | 852 | 400 | 247 | 147 | 390 | 480 | 960 | 360 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.6746 | 2.1469 | 2.6212 | 1.9378 | 0.86124 | 0.86124 | 0.35885 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 3.445 | 2.2967 | 1.2919 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 1 | 18 | 6 | 12 | 6 | 30 | 4 | 6 | 6 | 18 | 1 | 8 | 1 | 8
Total flow | lt/min | 331.4 | 20.7 | 20.7 | 72 | 12 | 12 | 4 | 36 | 30 | 24 | 24 | 60 | 16 | 12 | 36 | 72 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 34696 | 3096 | 3780 | 9720 | 720 | 720 | 100 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 2880 | 5760 | 6480 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [9 empty] | 4800
Pressure drop (measured) | bar | [6 empty] | 1.6? |  | 10.5psi/lvps | [5 empty] | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 297.4
Total Heat removed | W | 34.696
Total temperature rise | C | 1.6746
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192

## Present YE2
YE2 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 152.8 | 2.3 | 2.3 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.6049 | 0.78256 | 0.78256 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 69716.5351 | 5972.7244 | 5972.7244 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W
# chambers/circuit | #
Heat removal/circuit | W | 27032 | 327 | 390 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.5394 | 2.0408 | 2.434 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 0 | 4 | 2 | 4
Total flow | liter/min | 152.8 | 55.2 | 27.6 | 0 | 20 | 10 | 40
Heat removed | W | 27032 | 7848 | 4680 |  | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 0
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 152.8
Total Heat removed | kW | 27.032
Total temperature rise | C | 2.5394

## Upgr YE2 LS2
YE2 UPGRADE cooling parameters |  |  |  | LS2
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 173.2 | 2.3 | 4 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.8192 | 0.78256 | 1.361 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 79024.2401 | 5972.7244 | 10387.3467 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 0 | 260 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 | 3 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 31712 | 327 | 780 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.6282 | 2.0408 | 2.799 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 |  | 4 | 2 | 4
Total flow | liter/min | 185.2 | 55.2 | 48 | 12 | 20 | 10 | 40
Heat removed | W | 31736 | 7848 | 9360 | 24 | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 0
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 173.2
Total Heat removed | W | 31.736
Total temperature rise | C | 2.6301

## Upgr YE2 LS3
YE2 UPGRADE cooling parameters |  |  |  | LS2
IN LS3 NO CHANGES WITH RESPECT TO LS2 on YE2 | ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 173.2 | 2.3 | 4 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.8192 | 0.78256 | 1.361 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 79024.2401 | 5972.7244 | 10387.3467 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 0 | 260 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 | 3 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 31712 | 327 | 780 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.6282 | 2.0408 | 2.799 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 |  | 4 | 2 | 4
Total flow | liter/min | 185.2 | 55.2 | 48 | 12 | 20 | 10 | 40
Heat removed | W | 31736 | 7848 | 9360 | 24 | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 0
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 173.2
Total Heat removed | kW | 31.736
Total temperature rise | C | 2.6301

## Present YE3
YE3 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 198.8 | 2.3 | 2.3 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.0881 | 0.78256 | 0.78256 | 1.1795 | 1.1795 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 90704.4973 | 5972.7244 | 5972.7244 | 6837.8172 | 6837.8172 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  |  | 123 | 20 | 20
# chambers/circuit | # |  |  | 3 | 4 | 4
Heat removal/circuit | W | 21666 | 360 | 369 | 80 | 80 |  | 426 | 1000 | 2516
Temperature rise | C | 1.5644 | 2.2467 | 2.3029 | 0.57416 | 0.57416 | 0 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 12 | 4 | 3 | 3
Total flow | liter/min | 198.8 | 27.6 | 13.8 | 36 | 36 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 21666 | 4320 | 2214 | 1440 | 1440 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [5 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 198.8
Total Heat removed | kW | 21.666
Total temperature rise | C | 1.5644
Note on F13: paola tropea: From Salvatore's mail Feb 2016
Note on G13: paola tropea: From Salvatore's mail Feb 2016

## Upgrade YE3 LS2
YE3 UPGRADE cooling parameters |  |  |  | Replacement of electronics LS2
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 28 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 227 | 2.3 | 4 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.3843 | 0.78256 | 1.361 | 1.1795 | 1.1795 | 1.2 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 103571.0306 | 5972.7244 | 10387.3467 | 6837.8172 | 6837.8172 | 6838 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 0 | 260 | 20 | 20 | 20 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 | 3 | 5 | 4 | 2 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 24852 | 360 | 780 | 100 | 80 | 40 |  | 426 | 1000 | 2516
Temperature rise | C | 1.5715 | 2.2467 | 2.799 | 0.7177 | 0.57416 | 0.2 | 0 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 9 | 12 | 4 | 3 | 3
Total flow | liter/min | 227 | 27.6 | 24 | 36 | 36 | 18 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 24852 | 4320 | 4680 | 1800 | 1440 | 360 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [6 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 227
Total Heat removed | kW | 24.852
Total temperature rise | C | 1.5715
ME4/1heat per circuit rises to 780 W instead of 370 W
RPC upgrade chambers to be installed btween LS2 and LS3
The RE3/1 cooling is taken off the RE3/2 and RE3/3 system so there is no more flow and a minimal 0.1degC increase
1 chamber more per cooling circuit on RE3 spigots
The RE4/1 cooling is taken off the mini-manifolds of the other RE4 stations, using "T"s with 9 circuits out of 18 existing, giving a similar temp increase as the RE3 station.
The YE3 manifold flow rate increase is half of the RE3 station namely 18 litres/min on a total of 161 [litres/min] .

## Upgrade YE3 LS3
YE3 UPGRADE cooling parameters
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 28 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 227 | 2.3 | 4 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.3843 | 0.78256 | 1.361 | 1.1795 | 1.1795 | 1.2 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 103571.0306 | 5972.7244 | 10387.3467 | 6837.8172 | 6837.8172 | 6838 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 0 |  | 20 | 20 | 20 | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 |  | 5 | 4 | 2 | 0 | 0 | 0 | 0
Heat removal/circuit | W | 24852 | 360 | 780 | 100 | 80 | 40 |  | 426 | 1000 | 2516
Temperature rise | C | 1.5715 | 2.2467 | 2.799 | 0.7177 | 0.57416 | 0.2 | 0 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 9 | 12 | 4 | 3 | 3
Total flow | liter/min | 227 | 27.6 | 24 | 36 | 36 | 18 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 24852 | 4320 | 4680 | 1800 | 1440 | 360 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [6 empty] | 0
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 227
Total Heat removed | kW | 24.852
Total temperature rise | C | 1.5715