## Timeline
2016-02-02 | Original file by Armando
2016-02-05 | Modification by PT to split Rack and Encap cooling circuit power/flow
2016-02-09 | Data updated for RPC (mail of Salvatore)
2017-07-19 | Upgrade needs added on Micha input
2017-07-20 | Micha input on details for CSC, Andrey input on GEMs

## Summary
YE+1 and YE-1 |  | Present | Upgrade summary (keeping constant flow)
Total flow-disk manifold | liter/min | 662.8 | 662.8
Total Heat removed | W | 66280 | 114680
Total temperature rise | C | 1.4354 | 2.4836
YE+2 and YE-2
Total flow | liter/min | 353.6 | 353.6
Total Heat removed | W | 54064 | 63424
Total temperature rise | C | 2.1947 | 2.5746
YE+3 & YE-3
Total flow | liter/min | 397.6 | 397.6
Total Heat removed | W | 43332 | 49920
Total temperature rise | C | 1.5644 | 1.8022
FULL ENDCAP CIRCUIT 2*YE1+2*YE2+2*YE3
Total flow | liter/min | 1414
Total Heat removed | W | 163676
Total temperature rise | C | 1.6615
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4
Total Heat removed | W | 28200
Total temperature rise | C | 2.2192
Flow-Heat Summary for full circuit
ENDCAP circuit for 6 disks
| Units | Needs 2017 | Measures '17 | Upgrade needs
Total flow | liter/min | 1414 | 1266.6667 | 1414
Total flow | m3/h | 84.84 | 76 | 84.84
Total Heat | W | 163676 | 105893.3333 | 228024
Total temperature rise | C | 1.6615 | 1.2 | 2.3148
Note on D34: paola tropea: From EN-CV flowmeter
Note on D35: paola tropea: Calculated from DT and Flow measurements
Note on D36: paola tropea: From main circuit T readings

## Present YE1
YE1 cooling parameters
| ENDCAP COOLING CIRCUIT | [14 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | GEM cooling circuit GE1/1- demostrator | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 1586.8003 | 585.0526 | 1586.8003 | 585.0526
Flow rate | liter/min | 331.4 | 2.3 | 2.3 | 4 | 2 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.1641 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 1.1795 | 2.359 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 119224.0949 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 6837.8172 | 13675.6345 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber | W |  |  |  |  | 200 | 20 | 20 | 25 | ?
# chambers/circuit | # |  |  |  |  | 2 | 6 | 6 | 4 | ?
Heat removal/circuit | W | 33140 | 344 | 420 | 540 | 400 | 120 | 120 | 100 | 80 | 852 | 400 | 247 | 147 | 390 |  | 1775 | 14000 | 1750
Temperature rise | C | 1.4354 | 2.1469 | 2.6212 | 1.9378 | 2.8708 | 0.86124 | 0.86124 | 0.35885 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 2.5 | 6 | 6 | 1 | 18 | 6 | 12 | 6 | 30 | 4 | 1 | 8 | 1 | 8
Total flow | lt/min | 337.4 | 20.7 | 20.7 | 72 | 6 | 12 | 12 | 4 | 36 | 30 | 24 | 24 | 60 | 16 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 33140 | 3096 | 3780 | 9720 | 1000 | 720 | 720 | 100 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [10 empty] | 4800
Pressure drop (measured) | bar | [7 empty] | 1.6? |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 331.4
Total Heat removed | W | 33140
Total temperature rise | C | 1.4354
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192

## Present YE2
YE2 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 176.8 | 2.3 | 2.3 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 1.857 | 0.78256 | 0.78256 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 80666.7762 | 5972.7244 | 5972.7244 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W
# chambers/circuit | #
Heat removal/circuit | W | 27032 | 327 | 390 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.1947 | 2.0408 | 2.434 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 176.8 | 55.2 | 27.6 | 24 | 20 | 10 | 40
Heat removed | W | 27032 | 7848 | 4680 |  | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 4800
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 176.8
Total Heat removed | W | 27032
Total temperature rise | C | 2.1947

## Present YE3
YE3 cooling parameters
ENDCAP COOLING CIRCUIT
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE4 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 198.8 | 2.3 | 2.3 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.0881 | 0.78256 | 0.78256 | 1.1795 | 1.1795 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 90704.4973 | 5972.7244 | 5972.7244 | 6837.8172 | 6837.8172 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  |  |  | 20 | 20
# chambers/circuit | # |  |  |  | 4 | 4
Heat removal/circuit | W | 21666 | 360 | 369 | 80 | 80 | 400 | 426 | 1000 | 2516
Temperature rise | C | 1.5644 | 2.2467 | 2.3029 | 0.57416 | 0.57416 | 2.8708 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 12 | 4 | 3 | 3
Total flow | liter/min | 198.8 | 27.6 | 13.8 | 36 | 36 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 21666 | 4320 | 2214 | 1440 | 1440 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [5 empty] | 4800
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 198.8
Total Heat removed | W | 21666
Total temperature rise | C | 1.5644
Note on F13: paola tropea: From Salvatore's mail Feb 2016
Note on G13: paola tropea: From Salvatore's mail Feb 2016

## Upgrade YE1
YE1 UPGRADE cooling parameters | [14 empty] | LS2 | LS3 | LS3
| ENDCAP COOLING CIRCUIT | [16 empty] | RACK COOLING CIRCUIT
| Units | TOTAL YE1 periphery manifold | CSC cooling circuit ME/1/3 | CSC cooling circuit ME/1/2 | CSC cooling circuit ME/1/1 | RPC cooling circuit RE1/3 | RPC cooling circuit RE1/2 | RPC cooling circuit RE1/1, RBX | RPC cooling circuit RE2 | VME/CRB circuit (minirack) | Disk circuit | HE cable tray/link boards | HE cable tray | LV periphery cable tray | GEM cooling circuit GE1/1 | GEM cooling circuit GE2/1 | GEM cooling circuit ME0 | YE1 +X tower manifold | Rack cooling circuit | YE1 -X tower manifold | Rack cooling circuit
Tube/pipe OD | mm | 60.32 | 9.5 | 9.5 | 9.5 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 10 | 10 | 10 | 8 | 8 | 10 | 48.26 | 33.7 | 48.26 | 33.7
Tube/pipe wall | mm | 1.65 | 0.76 | 0.76 | 0.76 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1 | 1 | 1 | 1 | 1 | 1 | 1.65 | 3.2 | 1.65 | 3.2
Tube/pipe ID | mm | 57.02 | 7.98 | 7.98 | 7.98 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 8 | 8 | 8 | 6 | 6 | 8 | 44.96 | 27.3 | 44.96 | 27.3
Tube/pipe Area | mm2 | 2552.2551 | 49.9891 | 49.9891 | 49.9891 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 50.24 | 50.24 | 50.24 | 28.26 | 28.26 | 50.24 | 1586.8003 | 585.0526 | 1586.8003 | 585.0526
Flow rate | liter/min | 331.4 | 2.3 | 2.3 | 4 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 2 | 4 | 2 | 2 | 4 | 91.2 | 11.4 | 91.2 | 11.4
Flow velocity | m/sec | 2.1641 | 0.76683 | 0.76683 | 1.3336 | 1.1795 | 1.1795 | 2.359 | 1.1795 | 1.0164 | 0.40654 | 1.327 | 0.66348 | 1.327 | 1.1795 | 1.1795 | 1.327 | 0.9579 | 0.32476 | 0.9579 | 0.32476
Reynolds | unitless | 119224.0949 | 5912.3984 | 5912.3984 | 10282.4319 | 6837.8172 | 6837.8172 | 13675.6345 | 6837.8172 | 10035.9353 | 4014.3741 | 10256.7258 | 5128.3629 | 10256.7258 | 6837.8172 | 6837.8172 | 10256.7258 | 41610.9163 | 8566.0568 | 41610.9163 | 8566.0568
Heat removal/chamber-superchamber | W |  | 0 | 0 | 0 | 20 | 20 | 25 | ? | 0 | 0 | 0 | 0 | 0 | 200 | 400 | 600
# chambers/circuit |  |  | 0 | 0 | 0 | 6 | 6 | 4 | ? | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1
Heat removal/circuit | W | 57340 | 344 | 420 | 540 | 120 | 120 | 100 | 80 | 852 | 400 | 247 | 147 | 390 | 400 | 400 | 600 |  | 1775 | 14000 | 1750
Temperature rise | C | 2.4836 | 2.1469 | 2.6212 | 1.9378 | 0.86124 | 0.86124 | 0.35885 | 0.57416 | 2.4459 | 2.8708 | 0.88636 | 1.055 | 1.3995 | 2.8708 | 2.8708 | 2.1531 | 0 | 2.235 | 2.2035 | 2.2035
Number of circuits | ea | 1 | 9 | 9 | 18 | 6 | 6 | 1 | 18 | 6 | 12 | 6 | 30 | 4 | 18 | 18 | 18 | 1 | 8 | 1 | 8
Total flow | lt/min | 331.4 | 20.7 | 20.7 | 72 | 12 | 12 | 4 | 36 | 30 | 24 | 24 | 60 | 16 | 36 | 36 | 72 | 91.2 | 91.2 | 91.2 | 91.2
Heat removed | W | 57340 | 3096 | 3780 | 9720 | 720 | 720 | 100 | 1440 | 5112 |  | 1482 | 4410 | 1560 | 7200 | 7200 | 10800 | 14200 | 14200 | 14000 | 14000
Heat removal capacity | W | [9 empty] | 4800
Pressure drop (measured) | bar | [6 empty] | 1.6? |  | 10.5psi/lvps | [5 empty] | 1.6?
ENDCAP CIRCUIT - same for YE+1 & YE-1
Total flow-disk manifold | liter/min | 331.4
Total Heat removed | W | 57340
Total temperature rise | C | 2.4836
RACK CIRCUIT - same for YE+1 & YE-1
Total flow-tower manifold | liter/min | 182.4 | Note: I believe that this number is uncertain because there are no flow restrictors in tower circuits.
Total Heat removed | W | 28200 | Note: Unpdated on Sept. 6,2007 to agree with Sergei's rack layout dated May 8,2007. Rack heat removals based on average requirement.
Total temperature rise | C | 2.2192
Note on P12: paola tropea: 2 superchambers/circuit (4 chambers in total in series)
Note on Q12: paola tropea: 1 superchamber/circuit
Note on R12: paola tropea: 6 chambers @ 100 W each in parallel

## Upgrade YE2
YE2 UPGRADE cooling parameters |  |  |  | LS2
ENDCAP COOLING CIRCUIT
| Units | YE2 periphery manifold | CSC cooling circuit ME2/2, ME3/2 | CSC cooling circuit ME2/1, ME3/1 | Disk circuit | VME/ circuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 197.2 | 2.3 | 4 | 2 | 5 | 5 | 10
Flow velocity | m/sec | 2.0713 | 0.78256 | 1.361 | 0.40654 | 1.0164 | 1.0164 | 2.0327
Reynolds | unitless | 89974.4812 | 5972.7244 | 10387.3467 | 4014.3741 | 10035.9353 | 10035.9353 | 20071.8705
Heat removal/chamber | W |  | 0 |  | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 |  | 0 | 0 | 0 | 0
Heat removal/circuit | W | 31712 | 327 | 780 | 400 | 852 | 852 | 2348
Temperature rise | C | 2.3083 | 2.0408 | 2.799 | 2.8708 | 2.4459 | 2.4459 | 3.3703
Number of circuits | ea | 1 | 24 | 12 | 12 | 4 | 2 | 4
Total flow | liter/min | 197.2 | 55.2 | 48 | 24 | 20 | 10 | 40
Heat removed | W | 31712 | 7848 | 9360 |  | 3408 | 1704 | 9392
Heat removal capacity | W |  |  |  | 4800
Pressure drop (measured) | bar |  | 2-4 |  |  | 10.5psi/lvps
ENDCAP CIRCUIT - same for YE+2 & YE-2
Total flow | liter/min | 197.2
Total Heat removed | W | 31712
Total temperature rise | C | 2.3083

## Upgrade YE3
YE3 UPGRADE cooling parameters |  |  |  | Replacement of electronics LS2
[6 empty] | New chambers LS3 |  | New chambers LS3
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3 | RPC cooling circuit RE3/1 | RPC cooling circuit RE4 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | 8 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 | 1 | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28 | 28.26 | 28 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 209 | 2.3 | 4 | 2 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.1952 | 0.78256 | 1.361 | 1.1795 | 1.2 | 1.1795 | 1.2 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 95358.3497 | 5972.7244 | 10387.3467 | 6837.8172 | 6838 | 6837.8172 | 6838 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/chamber | W |  | 0 |  | 20 |  | 20 |  | 0 | 0 | 0 | 0
# chambers/circuit | # |  | 0 |  | 4 |  | 4 |  | 0 | 0 | 0 | 0
Heat removal/circuit | W | 24960 | 360 | 780 | 80 | 23 | 80 | 23 | 400 | 426 | 1000 | 2516
Temperature rise | C | 1.7142 | 2.2467 | 2.799 | 0.57416 | 0.2 | 0.57416 | 0.2 | 2.8708 | 1.301 | 3.0541 | 3.8016
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 18 | 18 | 12 | 4 | 3 | 3
Total flow | liter/min | 209 | 27.6 | 24 | 36 | N/A | 36 | N/A | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 24960 | 4320 | 4680 | 1440 | 414 | 1440 | 414 |  | 1704 | 3000 | 7548
Heat removal capacity | W | [7 empty] | 4800
Pressure drop (measured) | bar
ENDCAP CIRCUIT - same for YE+3 & YE-3
Total flow | liter/min | 209
Total Heat removed | W | 24960
Total temperature rise | C | 1.7142
Note on F13: paola tropea: From Salvatore's mail Feb 2016
Note on H13: paola tropea: From Salvatore's mail Feb 2016