## YE3 Flow calculations
YE3 cooling parameters
| Units | YE3 periphery manifold | CSC cooling circuit ME4/2 | CSC cooling circuit ME4/1 | RPC cooling circuit RE3/2 | RPC cooling circuit RE3/1 | RPC cooling circuit RE4/2 | RPC cooling circuit RE4/1 | Disk circuit | VME/CRBcircuit (minirack) | Rack cooling circuit (low flow) | Rack cooling circuit (high flow)
Tube/pipe OD | mm | 48.26 | 9.525 | 9.525 | 8 | 8 | 8 | ~15 | 12.7 | 12.7 | 12.7 | 12.7
Tube/pipe wall | mm | 1.65 | 0.8128 | 0.8128 | 1 | 1 | 1 |  | 1.24 | 1.24 | 1.24 | 1.24
Tube/pipe ID | mm | 44.96 | 7.8994 | 7.8994 | 6 | 6 | 6 | 6 | 10.22 | 10.22 | 10.22 | 10.22
Tube/pipe Area | mm2 | 1586.8003 | 48.9844 | 48.9844 | 28.26 | 28.26 | 28.26 | 28.26 | 81.992 | 81.992 | 81.992 | 81.992
Flow rate | liter/min | 209 | 2.3 | 4 | 2 | 2 | 2 | 2 | 2 | 4.7 | 4.7 | 9.5
Flow velocity | m/sec | 2.1952 | 0.78256 | 1.361 | 1.1795 | 1.1795 | 1.1795 | 1.1795 | 0.40654 | 0.95538 | 0.95538 | 1.9311
Reynolds | unitless | 95358.3497 | 5972.7244 | 10387.3467 | 6837.8172 | 6837.8172 | 6837.8172 | 6837.8172 | 4014.3741 | 9433.7792 | 9433.7792 | 19068.277
Heat removal/circuit | W | 24362.8 | 360 | 780 | 34 | 23.3 | 34 | 23.3 | 400 | 550 | 1000 | 2700
Temperature rise | C | 1.6732 | 2.2467 | 2.799 | 0.24402 | 0.16722 | 0.24402 | 0.16722 | 2.8708 | 1.6797 | 3.0541 | 4.0796
Number of circuits | ea | 1 | 12 | 6 | 18 | 18 | 18 | 18 | 12 | 4 | 3 | 3
Total flow | liter/min | 245 | 27.6 | 24 | 36 | NA | 36 | 36 | 24 | 18.8 | 14.1 | 28.5
Heat removed | W | 24362.8 | 4320 | 4680 | 612 | 419.4 | 612 | 419.4 |  | 2200 | 3000 | 8100
Heat removal capacity | W | [7 empty] | 4800
Pressure drop (measured) | bar
Total flow | liter/min | 209
Total Heat removed | W | 24362.8
Total temperature rise | C | 1.6732 |  |  |  | ONE ENDCAP