## Slide 1
Cooling components and unions for RE4/1 cooling
Ian, 20 April 2018

## Slide 2
Diagram of 1 channel per 2 chambers. Flexible hose from the “T” mounted on the mini manifold.
The two RE4/1s will also be linked by flexibles.
RE4/1
Supply
Return
RE4/1 Cooling manifolds
Manifold

## Slide 3
Mini manifold . To be modified to accept the necessary “T”s for the RE4/1 cooling.
The same flow regulators will be kept with individual cut off valves to each chamber, if costs permit.

## Slide 5
This list will be ordered, simplified , from the USA or from XX in P5 in inch size.

## Slide 13
R
R
F
H
S
Q
Return Manifold

## Slide 14
J
H
I
F
Supply Manifold
“MPT” should be “NPT”

## Slide 15
P
N
O
8mm
Chamber fittings
K
L
M

## Slide 16
Modified Supply Manifold
A
H
J
J
H
A
41.08.84.404.6
NPT not MPT
T Parker "T" Female 1/4 NPT 4-4-4 FT-SS
A Bell & Gosset # RV -125A Readout valve
N Parker 216-4 1/4" hex nipple

## Slide 17
Modified Return Manifold
H
R
Q
Q
R
H
41.08.84.504.3
41.20.12.008.1
Not ¼” NPT
“Hayes” should be “Hays”
NPT not MPT
T Parker "T" Female 1/4 NPT 4-4-4 FT-SS
N Parker 216-4 1/4" hex nipple

## Slide 18
Supply Manifold

## Slide 19
Return Manifold

## Slide 20
Future Needs
Apollo 78-841 BV (Ball Valve) ¼” & stem & Port
Hayes 2305-1021 ¼” flow regulator
Parker 216-4 ¼” hex nipple
XX xxx ?? “T” 90deg to distribute flow
B&G RV—125A Readout Valve

## Slide 21
Components used in RE cooling and Mini-manifold

## Slide 23: Refs. CSC Dick and co
http://project-cms-rpc-endcap.web.cern.ch/project-cms-rpc-endcap/rpc/Services/Cooling/RE4cooling/MiniManiFold/RE4MiniManifold.zip
Then folder RE4 cooling, file “coolingYE3_26apr12”

## Slide 24
Power dissipated on chamber
30W per chamber
540W per station
1080W per Endcap
6 mini-manifolds for 18 chambers
3 chambers for 1 Mini-Mnifold
Each Mini Manifold has 3 channels
Each channel will me didvide into two.

## Slide 25
Apollo Valves
http://www.epmc.co.th/Valves/Apollo_pdfs/Apollo%20Ball%20Valve%20Numbering%20System.pdf
Full catalogue
https://www.cooneybrothers.com/ASSETS/DOCUMENTS/ITEMS/EN/Apollo_50GB-6A7A_Catalog.pdf
SS valves
https://www.parkersupply.com/images/siteAssets/pdf/Apollo_Ball_Valves_Catalog_-_APBVCA.pdf
Flow restrictors
Spelling “Hays” not Hayes !!
Hayes Mesurflo 2305-1021 ¼” flow regulator 0.5GPM ( gallons USA = XXX litres/ min)
http://flowcontrolvalves.haysfluidcontrols.com/viewitems/solenoid-valves/series-2305-mesurflo-automatic-flow-control
Full catalogue
http://famco.ca/wp-content/uploads/2013/07/Hays-Solenoid.pdf

## Slide 26
Read Out from port on “Apollo” ball valve probe
B&G (Bell and Gosset) RV-125A Readout valve ( diaphragm to be pierced by)
http://bellgossett.com/flow-balancing/flow-measurement/readout-valve-rv-125a-and-readout-probe-rp-250b/
https://shop.galloup.com/buy/product/rv-125a-b-g/3053529
https://www.statesupply.com/bi1311
https://media.statesupply.com/filemanager/1/8/1854.pdf

## Slide 27: RE3/1 cooling link to RE3/2
The rigid copper piping will be replaced by flexible hose links to reduce the strain on the unions.
x2 RE3/2 circuits feed x1 RE3/1 chamber

## Slide 28
Cooling
RE3/1
Verify the assembly of the flexibles with simplified safer version, namely direct from RE3/2 PP to RE3/1 PP with three elements only, as opposed to 3 times as many unions with a “L” Cu pipe producing a lever arm on the chamber PP.
RE4/1
Modify the present Mini-manifolds to take additional “take offs” direct to the chambers with flexibles all the way to the RE4/1 PP.

## Slide 29
Contacts
French Supplier
USA Supplier
CERN
27/1-003 76295 163618 Norbert.Frank@cern.ch
35/3-015 72968 161148 vincent.pittin@cern.ch