## Sheet1
| Power to FEB using standard CMS RE with 3 FEBs | [7 empty] | Anton Numbers 19 May 2016
[6 empty] | Ian Crotty | 2016-05-09 |  | For 10 FEBS
| Voltage | Current | Power | [5 empty] | Voltage | Current | Power
| [V] | [A] | [W] | [5 empty] | [V] | [A] | [W]
Digi | 7.5 | 1.43 | 10.725 |  |  |  |  | Digi | 7.5 | 2.64 | 19.8
Analogue | 7 | 0.73 | 5.11 |  |  |  |  | Analogue | 7 | 1.16 | 8.12
Power 2ch Digi & Analoge |  |  | 15.835 |  |  |  |  | Power |  |  | 27.92
Power for one chamber |  |  | 7.9175 |  |  |  |  | Power for one 10FEB chamber |  |  | 27.92
Power of 1 FEB (& dist board) |  |  | 2.6392 |  |  |  |  | Power of 1 FEB (& dist board) |  |  | 2.792
Power 36 chambers |  |  | 285.03 |  |  |  |  | Power for 18 Chambers |  |  | 502.56
Power 1 station |  |  | 570.06
Upscope for RE4/1 for 20 deg chambers
| 1 Eta division with 64 strips and 2 FEBs ( assume that Dist board power is included) | [6 empty] | Present RPC power on YE3
|  | Power = | 5.2783 |  | [watts] |  |  | No LBB in this Calculation
# Eta divisions |  | Power | Power 1 endcap |  |  |  |  | 36 x 4 = 144 chambers
[8 empty] | Total (x1) YE3 RPC Chamber Power |  |  |  | 1140.12 | [Watts]
|  | [W] | [W]
[6 empty] | % increase |  | From Anton 2016
2 |  | 10.5567 | 190.02 |  |  | 16.6667
3 |  | 15.835 | 285.03 |  |  | 25 |  | §Power Consumption/Currents (A)
4 |  | 21.1133 | 380.04 |  |  | 33.3333 |  | • LV_ANA 0.029A per chip, 0.116A per FEB, 1.16A per chamber
5 |  | 26.3917 | 475.05 |  |  | 41.6667 |  | • LV_DIG 0.066A per chip, 0.264A per FEB, 2.64A per chamber
6 |  | 31.67 | 570.06 |  |  | 50 |  | § Power Consumption/Dissipation (W)
• LV_ANA 0.203W per chip, 0.812W per FEB, 8.12W per chamber
• LV_DIG 0.495W per chip, 1.98W per FEB, 19.8W per chamber
PETIROC |  | (64 Channels) |  | There are two versions |  |  |  | • 2.792W per FEB, i.e. ~28W per chamber
tel call with Imad 24 may 2016
20 deg 320 strips. Read from both ends 640 Channels.
Channels | 640 |  | TDC in ASIC |  |  | FPGA TDC
|  |  | Power |  |  | Power
|  |  | [W] |  |  | [W]
Channel |  |  | 0.0036 |  |  | 0.08
20deg Ch |  |  | 2.304 |  |  | 51.2
20deg Ch |  | ? | 3 |  | ? | 3
20deg Ch |  | FPGA | 20 |  | DAQ | 21
20deg Ch |  | GBT | 1 |  |  | 1
1 | Chambers |  | 26.304 |  |  | 76.2
18 | chambers |  | 473.472 |  |  | 1371.6
DCC | 20W FPGA+GBT20W |  | 40 |  |  | 40 | DCC should be <5m from chambers !
Total for 1 station |  |  | 513.472 |  |  | 1411.6
DCC = Data Concentrator Card