## Slide 1: Power and Cooling RE
Ian Crotty 27 may 2016
Thanks to Sergei, Petr and Anton

## Slide 2: Contents
RPC requirements
Present loads on YE3 (ME4, RE3 & 4)
Future Up-scope loads

## Slide 3: Requirements
18- 22 deg C ( at 24 deg C RPCs are switched off.
Stable conditions
No leaks
Minimium operating pressure to achieve flow.

## Slide 4: How to achieve these conditions
Conductivity checks.
Annual Inspection and Tests.
Repairs ahead of time.
Correct assembly technics.
QA during upscope.
Early detection of leaks.
Ageing study of brass components.
More instrumentation eg; coolant temp on Manifold.

## Slide 5
2015 FOS Sensors stable apart interventions etc

## Slide 6
2016 FOS sensors
Start-up condition take time to stabilise

## Slide 7: Pressure in Manifold
YE-3 pressures
Delta P = 5.6bar

## Slide 8
Power in and Dissipation
Power to Racks
Power dissipated in Rack
Power dissipated from Chambers/Loads
Power to Load
Powertot = Rackdissip + Loaddissip

## Slide 9: Present configuration
One cooling circuit for Racks and Chambers on one YE3
Total Power on YE3 11748[W]
CSC Power 8890[W]
RPC Power 2852[W]
MAO Power 2564[W]

## Slide 10: Upscope Power Provisional values
FEB & LBB 2082W
Alternatives
PETIROC (embed) 1551W
PETIROC (FPGA) 4270W

## Slide 11: Provisional Conclusions
Temperatures has been stable over the years.
These are very provisional values
The full power system has to be studied for the alternatives.
RE3&4 is 46% of total Power on YE3
Upscope will add approx 25%