## Full Detail
Power in YE3 racks
|  |  | Sources | Lusin 0ct 2016
P. Levchenko
[9 empty] | Upgrade |  | Upgrade
Rack |  | P Required | P Dissipated | CSC P. | CSC FE P | RPC P. | RPC FEB P | RPC LB P | RPC | RPC | GRPC
|  | to chambers etc | in the racks | Rack |  | Rack
|  | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [W]
| Source | Lusin | Lusin
X5R51 |  | 0 | 426
X4A51 |  | 0 | 182 |  |  |  |  | XX
X3A51 |  | 5842 | 2506 |  |  | XX |  | XX
X2A52 |  | 0 | 182
X1R51 |  | 0 | 426
X5U51 |  | 0 | 426
X4J51 |  | 0 | 227
X3J51 |  | 5906 | 2527
X2J52 |  | 0 | 182
X1U51 |  | 0 | 426
Total YE+3 |  | 11748 | 7510
Power efficiency
0.63926
Rack |  | P Required | P Dissipated | CSC P. | CSC FE P | RPC P. | RPC FEB P | RPC LB P |  |  | GRPC
|  |  |  | Rack |  | Rack
|  | [W] | [W] | [W] | [W] | [W] | [W] | [W] |  |  | [W] | [W]
| Source | Lusin | Lusin
X5L51 |  | 0 | 426
X4S51 |  | 0 | 182
X3S51 |  | 5842 | 2506
X2S52 |  | 0 | 182
X1L51 |  | 0 | 426
X5E51 |  | 0 | 426
X4V51 |  | 0 | 227
X3V51 |  | 5906 | 2527
X2V52 |  | 0 | 182
X1E51 |  | 0 | 426
Total YE+3 |  | 11748 | 7510
Power efficiency
0.63926
Power required x 1.56 gives power dissipated
Total Power consummed = P req. + P Dissip
Total P for 2 YE3 disc = |  |  | 23496 | [W] | 25kW

## Simple View
Simplified power of one YE3
See sheet 1
[5 empty] | Present configuration | [7 empty] | Upscope
[5 empty] | Chambers |  | FEB Power in Racks |  |  |  | LBB Power Rack |  |  |  | FEB Power in Racks |  |  |  | PETIROC
| Total Rack power | Dissipated Power in racks | Total CSC power YE+3 |  | RE3/2 & 3/3 | RE4/2 & 4/3 | RE3 | RE4 | RE3 LBB | RE4LBB | RE3 LBB | RE4LBB | RE3/1 FEB | RE4/1 FEB | RE3 | RE4 | RE3/1LBB | RE4/1 LBB | RE3/1 TDC EmBed | RE4/1 TDC Embed | RE3&4 Embed | RE3/1 TDC FPGA | RE4/1 TDC FPGA | RE4 &3 FPGA Power
[21 empty] | Rack Power | [5 empty] | [W] | [W]
Source | Lusin | Lusin | P. Levchenko | [5 empty] | Anton | Anton | Anton | Anton | [6 empty] | Imad | Imad | Estimate | Imad | Imad |  | LBB Power |  | 85
| [W] | [W] | [W] |  | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [W] | [6 empty] | [W] | [W] | [W] | [W] | [W] | [W] | Dissipated in Easy Crate |  | 56
[17 empty] | estimate | estimate | [6 empty] | Efficiency |  | 0.65882
| 11748 | 7510 | 8867 |  | 570 | 570 | 291.84 | 291.84 | 340 | 340 | 224 | 224 | 502 | 502 | 257.024 | 257.024 | 282 | 282 | 513 | 513 | 525.312 | 1412 | 1412 | 1445.888
B=3.8 |  |  | 8890 | [21 empty] | Using data |  | Power 1 | 920
[25 empty] | At max load |  | Power 2 | 25
|  |  |  | Total power | [22 empty] | Dissipated | 320
|  |  |  | Present config Ch (432FEB) |  |  |  | 1723.68
|  |  |  | Present config LBB | [7 empty] | 1128 | [13 empty] | Efficiency |  | 0.66138
|  |  |  | Power Present config | [7 empty] | 2851.68
|  |  |  | Upscope FEB (360FEB) | [11 empty] | 1518.048
|  |  |  | Upscope LBB | [13 empty] | 564
|  |  |  | Tot Power Upscope FEB | [13 empty] | 2082.048
|  |  |  | Upscope TDC Emb | [16 empty] | 1551.312
|  |  |  | Upscope TDC FPGA | [19 empty] | 4269.888
Power tot = Lrack + L chamber
L rack = (Lch/0.66) - Lch
PS efficiency definition = output/input
Peff = Lch/powertot
[6 empty] | For 3009 | P1 + P2 = 945W @ max load
Dissipated power = 320W
Powertot - (Eff x Ptot) = PDisipRack
Powertot (1-Eff) = PDisipRack
Eff = 1-(320/945)
Eff = 0.6614
Eff = 66%
Chamber
Heat loss from Chamber
Heat Loss from Rack
Power to Chamber
Total Input Power
Rack

## MAO calc
Mao
Simplified Schematic of RE and LBB Power supply and distribution
There is a small (120W, <4%) discrepancy
here between the MAO in and out.
Overall power transmission efficiency in the UXC is approx 56%
Assumed efficiency for A3009 & A3016 of 66% as claimed by CAEN
MAO Efficiency is claimed to be 90% Eff and measured to max 88%
see;
lhcb-muon.web.cern.ch/lhcb-muon/electronics/LVPS%20Meeting%20100206-3.pps
LHC LVPS Procurement - Status
by Chris Parkman 2006
Also"A3009 show overall efficiencies of less than 60% at all loads"
MAO
2x 292 + 2x 224W = 1264W
2x570 + 2x 340W
= 1820W
3009 & 3016
Load, chamber and LBC
2x 1632 = 3264W
1264 + 1820 = 3084W
~300W

## Upscope Approx.
Simplified Schematic of RE and LBB Power supply and distribution after Upscope
Use scaling factor of (2x72x3) = 432 FEBs/(2x 18x10 = 360) = 0.833
Adding original config = 1.833
There is a small (120W, <2%) discrepancy
here between the MAO in and out.
Overall power transmission efficiency in the UXC is approx 56%
Assumed efficiency for A3009 & A3016 of 66% as claimed by CAEN
MAO Efficiency is claimed to be 90% Eff and measured to max 88%
see;
lhcb-muon.web.cern.ch/lhcb-muon/electronics/LVPS%20Meeting%20100206-3.pps
LHC LVPS Procurement - Status
by Chris Parkman 2006
Also"A3009 show overall efficiencies of less than 60% at all loads"
MAO
1264W x 1.833 = 2316W
1820 x 1.833 = 3336W
3009 & 3016
Load, chamber and LBC
3264W x 1.833 = 5983W
3084W x 1.833 = 5653W
~450W
OR 3336 + 2316 + 450 = 6102W.
Conclude at 6kW