## Slide 1
YE3
YE1
Panel iRPC
Patch
Panel
Mini Cable Chain
Main Cable Chain
Patch Panel
USC
USC Rack
iRPC
UXC
USC
iRPC: 4 fibers per chamber
Number of Chambers:
18 RE+3/1 -> 72 fibers
18 RE+4/1 -> 72 fibers
18 RE-3/1 -> 72 fibers
18 RE-4/1 -> 72 fibers
Trunk Cable 1
Trunk Cable 2
Proposal:
4 Trunk cable 1 (96 fibers: 72 used + 24 spares)
4 Trunk cable 2 (96 fibers: 72 used + 24 spares)
*1 cable per 18 chambers

## Slide 2
MTP/MPO connector
24 fibers per connector
Trunk cable option
12 fibers per connector
Male
Male
Female
Female

## Slide 3
Specification Trunk Cable 1 (96 fibers)
Specification Trunk Cable 2 (96 fibers)
Panel iRPC
Patch
Panel
Patch
Panel
Patch Panel
USC
4 MPT/MPO Connectors Female
3 used + 1 spare
(24 fiber per connector)
8 MPT/MPO Connectors Female
6 used + 2 spares
(12 fiber per connector)
4 MPT/MPO Connectors Male
3 used + 1 spare
(24 fiber per connector)
4 MPT/MPO Connectors Male
3 used + 1 spare
(24 fiber per connector)
Length B: 80 m.?
Length A: 1 m. ?
Length : 1 m. ?
Length B: 30 m.?
Length A: 1 m. ?
Length C: 1 m.?

## Slide 4: General Cable Requirements
96 fibers per cable
Multimode OM3
Jacket: Low Smoke Zero Halogen (LSZH)
Compliance with CERN IS23:
https://edms.cern.ch/document/335745/LAST_RELEASED/