## Slide 1: RPC Power System Review
Anton Dimitrov
30.Nov.2018, CERN

## Slide 2
The HV power system will be based on CAEN EASY system
(practically, extension of the existing HV system):
SY4527 – 1 (existing)
A3485S - 2 modules (existing)
4 EASY3000 crates
A3512N – 12 HV Boards
4 HV multiconductor cables per endcap. Each with 20 HV channels
All must go via the YE1’s main cable chains (MCC)
Long term maintenance will be secured by CERN-CAEN contract.
To be integrated in the RPC DCS.
A3512N
A3485S
SY4527
EASY3000
HV Power System Upgrade for RE3/1 & RE4/1 (I)
USC
UXC
TDR Baseline: Variant I
1

## Slide 3
A3485S
A3485S
A3485S
A3485S
SY4527
SY4527
S1H07
HEX
HEX
ENDCAP RACKS S1H11 – S1H08
Crate4
RE-3/1 RE-4/1
Crate4
RE+3/1 RE+4/1
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HEX
HEX
S1H12
HV Distribution Box
HV Distribution Box
48V DC cable connected after Crate3 in rack S1H09
48V DC cable connected after Crate3 in rack S1H11
1 new rack (already defined S1H12, to be equipped)
2 EASY crates
8 umbilical cables all arriving to one rack
6 A3512N HV boards in each Crate (12 boards in total)
8 HV Distributor Boxes in total (all in one rack)
2

## Slide 4
The HV power system will be based on CAEN NON-EASY system:
SY4527 – 2 (new)
New HV boards – prototype ready in 2019
4 HV multiconductor cables per endcap. Each with 20 HV channels
All must go via the YE1’s main cable chains (MCC)
Long term maintenance will be secured by CERN-CAEN contract.
To be integrated in the RPC DCS.
New boards
SY4527
HV Power System Upgrade for RE3/1 & RE4/1 (II)
USC
UXC
Preferred Variant: Variant II
3

## Slide 5
A3485S
A3485S
A3485S
A3485S
SY4527
SY4527
S1H07
HEX
HEX
ENDCAP RACKS S1H11 – S1H08
HV Distribution Box
HEX
HEX
S1H12
- No EASY system  no EASY crates
- 2 SY4527 mainframes more
- 8 umbilical cables all arriving to one rack
- New type of HV boards!
- 8 HV Distributor Boxes in total (all in one rack), but bigger in size since all inputs and outputs should be at the back side of the rack
- No rack cross reference in DSS Action Matrix
SY4527
SY4527
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
HV Distribution Box
4

## Slide 6
24 A3016 LV boards in total to power the FE of all RE3/1 and RE4/1 chambers.
9U in each YE3 X4Far tower rack for
  1 CAEN EASY3000S crate
  1 CAEN A3486S MAO- AC/DC 48V PS
15U in each X2Near YE3 tower rack for
  2 CAEN EASY3000S crates
  1 CAEN A3486S MAO- AC/DC 48V PS
SY4527 with A1676A
CAEN EASY3000S
with CAEN A3016 in X2Near && X4Far racks
A3486S
48V Service power
50p Communication bus
USC
UXC
YE1 LV PP
RPC LV Power System for RE3/1 & RE4/1
5
going directly to YE3
Relay
YE+3: X2J52, X3J51, X3A51, X4A51
YE-3: X2V52, X3V51,X3S51, X4S51
Existing RE3&RE4 detector

## Slide 7
mini Cable Chains for OF
LV Easy crates
Near Side
Far Side
mini Cable Chains for OF
LV Easy crates
X2
X4
RPC LV Services
6
X2Near – X4Far diagonal

## Slide 8
Air Deflector
HEX
X2J52
RE3 LBB
Cable Distribution
RE A3486S AC/DC-0 CH0 CH1
EMU Maraton
EMU Maraton
Turbine
Power Distribution
X3J51
X4A51
YE+3
Near Side
Far Side
RE4 LBB
HEX
HEX
RE3-4/1 FE EASY3000S Crate0
HEX
Turbine
Power Distribution
EMU
EMU VME
Air Deflector
HEX
RE3 LBB
Cable Distribution
RE3-4 FEB EASY3000S Crate1
RE3-4 LBB EASY3000S Crate2
RE A3486S AC/DC-1 CH0 CH1
RE4 LBB
Power Dist.
Power Dist.
Power Dist.
HEX
Turbine
Power Distribution
RE3 LBB
RE4 LBB
EMU Maraton
HEX
EMU Maraton
HEX
Air Deflector
Alignment DAQ
RE3-4/1 FE EASY3000S Crate2
RE A3486S AC/DC-1 CH0 CH1
Power Dist.
HEX
Turbine
Power Distribution
HEX
Air Deflector
RE4 LBB
RE4 LBB
Cable Distribution
RE3-4 LBB EASY3000S Crate1
RE3-4 FEB EASY3000S Crate0
RE A3486S AC/DC-0 CH0 CH1
X3A51
EMU
EMU VME